## 諸元マスター
| 15 | 25 | [16 empty] | 20 | 40
Sheet | 製品名 | コンポーネント | Unit数 (U) | 台数 | 外寸:高さ (cm) | 外寸:幅 (cm) | 外寸:奥行 (cm) | 重量 (kg) | 消費電力 (W) | 消費電力 (VA) | 電流(A) 100V | 電流(A) 200V | 発熱量 (BTU/hr) | 電圧 (V) | 温度 (℃) | 湿度 (%) | 接続 コネクタ数 | PSU コネクタ形状 | ケーブル形状 | 備考
Rack | Rack
Rack | 40U CLARiX Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | EC-1700-B Rack | システム一式 | 40 | - | 194.7 | 76.708 | 106.3752 | 219 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30 | EC-1700 *Inchからcmに換算した結果を表記 ☆broadcomのダイレクタswitchをのせるrack。PDU付き。40U-Cと同じPDU。C19が各PDUに一口ずつ。
Rack | EC-1700-C Rack | システム一式 | 40 | - | 194.7 | 76.708 | 106.3752 | 219 | - | - | - | - | - | - | - | - | - | - | - | EC-1700 *Inchからcmに換算した結果を表記 ☆ciscoのダイレクタswitchをのせるrack。PDUなし。
Rack | EC-1900-CTX | システム一式 | 42 | - | 202.95 | 70.36 | 129.29 | 273.06 | - | - | - | - | - | - | - | - | - | - | - | EC-1900-CTX *Inchからcmに換算した結果を表記 ☆のダイレクタをのせるrack。PDUなし。
Rack | PowerStore Rack | システム一式 | 40 | - | 190.8 | 61.1 | 99.2 | 173 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P
Rack | PowerStore Rack | システム一式 | 42 | - | 199.13 | 60 | 99.8 | 176 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P
Rack | 40U-C Unity Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | 40U-C VNX Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30 | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | 40U-D VNX Rack | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 6 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | 40U VPLEX V1/V2 Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | *40U-C Rack *Inchからcmに換算した結果を表記
Rack | 40U VPLEX VS6 Rack | システム一式 | 40 | - | 190 | 60.96 | 99.98 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | Centera Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | 40U DD Rack | システム一式 | 40 | - | 190.8 | 61.1 | 99.2 | 173 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | 40U AVAMAR Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | 42U AVAMAR Rack | システム一式 | 42 | - | 199.16 | 60 | 120 | 232.02 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 42U Titan S Rack ※※The empty rack weight includes Cabinet, Pallet, side panels, Packaging
Rack | 40U XtreamIO Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.98 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | X2 Rack 40U | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | 44U XtreamIO Rack | システム一式 | 44 | - | 210.82 | 69.85 | 122.174 | 209.56 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | X02-RACK-44U
Rack | 42U PowerMax2500 Rack | システム一式 | 42 | - | 199.16 | 60 | 114.8 | 232.02 | - | - | - | - | - | - | - | - | 単相/12_三相2 | - | NEMAL6-30P | 42U Titan S Rack ※※The empty rack weight includes Cabinet, Pallet, side panels, Packaging
Rack | 42U PowerMax8500 Rack | システム一式 | 42 | - | 199.16 | 60 | 120 | 232.02 | - | - | - | - | - | - | - | - | 単相/12_三相2 | - | NEMAL6-30P | 42U Titan S Rack ※※The empty rack weight includes Cabinet, Pallet, side panels, Packaging
Rack | Isilon Rack Gen5シリーズ | システム一式 | 40 | - | 190.5 | 60.96 | 99.98 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | Isilon Rack Gen6シリーズ | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | Isilon Rack A2000 /H5600 only | システム一式 | 42 | - | 201.93 | 71.2 | 121.92 | 250 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 42U-HD Rack ※The empty rack weight includes frame, rear door, side panels, top & bottom access panels, up to 4 PDUs (depending on the PDU type), etc…
Rack | 42U ECS Gen3 EX5000 | システム一式 | 42 | - | 199.16 | 60 | 120 | 232.02 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 42U Titan S Rack ※※The empty rack weight includes Cabinet, Pallet, side panels, Packaging
Rack | 40U ECS Gen3 EX300/EX500/EXF900 | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 単相/4 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | 40U ECS Gen3 EX3000 | システム一式 | 40 | - | 190.5 | 60.96 | 134.62 | 218.632 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 40U-D CABOOSE Rack *Inchからcmに換算した結果を表記
Rack | 40U ECS Gen2 Dシリーズ | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | 40U ECS Gen1/Gen2 Uシリーズ | システム一式 | 40 | - | 190.5 | 60.96 | 111.76 | 198 | - | - | - | - | - | - | - | - | 単相/4 | - | NEMAL6-30P | 40U-D Rack *Inchからcmに換算した結果を表記
Rack | ScaleIO node Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.98 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | 40U Celerra Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 2 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | VxRack Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.98 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | VxRail Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | DP RACK | システム一式 | 40 | - | 190.8 | 61.1 | 99.2 | 173 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | MHC-RACK-1PH | システム一式 | 40 | - | 190.5 | 60.96 | 99.98 | - | - | - | - | - | - | - | - | - | 単相/6 | - | NEMAL6-30P | 40U-P Rack *Inchからcmに換算した結果を表記
Rack | Dlm8500 Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Rack | Dlm8100 Rack | システム一式 | 40 | - | 190.5 | 60.96 | 99.99 | 176.904 | - | - | - | - | - | - | - | - | 4 | - | NEMAL6-30P | 40U-C Rack *Inchからcmに換算した結果を表記
Unity | Unity XT
Unity | XT METRO | Unity XT metro node #1 | 1 | - | 4.28 | 48.2 | 80.85 | 29.9 | 750 | 789.4737 | 7.8947 | 3.9474 | 2559.11 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | 定格:750W / Input power consumption:271W
Unity | XT ALL FLASH | 380F DPE 2.5" | 2 | - | 8.88 | 44.76 | 61.39 | 28 | 970.5 | 1007 | 10.07 | 5.04 | 3311 | 100-240 | 5-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 480F DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 42 | 1050 | 1060 | 10.6 | 5.3 | 3581 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 |  | diskフル搭載
Unity |  | 680F DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 42 | 1161 | 1172 | 11.72 | 5.86 | 3960 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 |  | diskフル搭載
Unity |  | 880F DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 42 | 1411.96 | 1440.77 | 14.41 | 7.2 | 4818 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 | C13/C14 | diskフル搭載 *100V:Requires customer supplied step-up transformer
Unity |  | 25x2.5"用拡張 DAE #1 | 2 | - | 8.46 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 5-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 80X2.5"用拡張 DAE #1 | 3 | - | 13.21 | 44.7 | 76.2 | 58.9 | 1233 | 1318 | 13.18 | 6.59 | 4207 | 100-240 | 5-35 | 20-80 | 4 | C14 |  | diskフル搭載※フル搭載でも100V対応しているがディスクの種類は限られます。
Unity | XT HYBRID | 380 DPE 2.5" | 2 | - | 8.88 | 44.76 | 61.39 | 30 | 970.5 | 1007 | 10.07 | 5.04 | 3311 | 100-240 | 5-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 480 DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 44 | 1050 | 1060 | 10.6 | 5.3 | 3581 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 |  | diskフル搭載
Unity |  | 680 DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 44 | 1161 | 1172 | 11.72 | 5.86 | 3960 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 |  | diskフル搭載
Unity |  | 880 DPE 2.5" | 2 | - | 8.72 | 44.72 | 79.55 | 44 | 1411.96 | 1440.77 | 14.41 | 7.2 | 4818 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 | C13/C14 | diskフル搭載 *100V:Requires customer supplied step-up transformer
Unity |  | 3.5"用拡張 DAE #1 | 3 | - | 13.33 | 44.45 | 35.56 | 30.8 | 281 | 313 | 2.9 | 1.6 | 959 | 100-240 | 5-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 25x2.5"用拡張 DAE #1 | 2 | - | 8.46 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 5-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 80X2.5"用拡張 DAE #1 | 3 | - | 13.21 | 44.7 | 76.2 | 58.9 | 1233 | 1318 | 13.18 | 6.59 | 4207 | 100-240 | 5-35 | 20-80 | 4 | C14 |  | diskフル搭載※フル搭載でも100V対応しているがディスクの種類は限られます。
Unity | Unity
Unity | ALL FLASH | 300F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 903.5 | 907.5 | 9.04 | 4.48 | 3083 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 350F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 970.5 | 1007 | 10.07 | 5.04 | 3311 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 400F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 905 | 909 | 9.09 | 4.55 | 3088 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 450F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 981 | 1017.6 | 10.18 | 5.09 | 3347 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 500F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 951 | 955 | 9.55 | 4.78 | 3245 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 550F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 1019 | 1055.6 | 10.56 | 5.28 | 3477 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 600F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 985 | 989 | 9.89 | 4.89 | 3361 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 650F DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 1061 | 1097.6 | 10.98 | 5.49 | 3620 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 25x2.5"用拡張 DAE #1 | 2 | - | 8.46 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 80X2.5"用拡張 DAE #1 | 3 | - | 13.21 | 44.7 | 76.2 | 58.9 | 1233 | 1318 | 13.18 | 6.59 | 4207 | 100-240 | 10-35 | 20-80 | 4 | C14 |  | diskフル搭載※フル搭載でも100V対応しているがディスクの種類は限られます。
Unity | HYBRID | 300 DPE 3.5" | 2 | - | 8.88 | 44.76 | 68.43 | 38 | 678.5 | 718.5 | 6.94 | 3.59 | 3313 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 300 DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 903.5 | 907.5 | 9.04 | 4.48 | 3083 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 400 DPE 3.5" | 2 | - | 8.88 | 44.76 | 68.43 | 38 | 681 | 720 | 6.95 | 3.6 | 2324 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 400 DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 905 | 909 | 9.09 | 4.55 | 3088 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 500 DPE 3.5" | 2 | - | 8.88 | 44.76 | 68.43 | 38 | 727 | 766 | 7.41 | 3.83 | 2481 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 500 DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 951 | 955 | 9.55 | 4.78 | 3245 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 600 DPE 3.5" | 2 | - | 8.88 | 44.76 | 68.43 | 38 | 761 | 800 | 7.8 | 4 | 2597 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 600 DPE 2.5" | 2 | - | 8.88 | 44.76 | 60.9 | 30 | 985 | 989 | 9.89 | 4.89 | 3361 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 3.5"用基本 DAE #1 | 3 | - | 13.33 | 44.45 | 35.56 | 30.8 | 281 | 313 | 2.9 | 1.6 | 959 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 3.5"用拡張 DAE #1 | 3 | - | 13.33 | 44.45 | 35.56 | 30.8 | 281 | 313 | 2.9 | 1.6 | 959 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 2.5"用基本 DAE #1 | 2 | - | 8.46 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 2.5"用拡張 DAE #1 | 2 | - | 8.46 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | diskフル搭載
Unity |  | 80X2.5"用拡張 DAE #1 | 3 | - | 13.21 | 44.7 | 76.2 | 58.9 | 1233 | 1318 | 13.18 | 6.59 | 4207 | 100-240 | 10-35 | 20-80 | 4 | C14 |  | diskフル搭載※フル搭載でも100V対応しているがディスクの種類は限られます。
PowerStore | PowerStore
PowerStore | PowerStore METRO | PowerStore metro node #1 | 1 | - | 4.28 | 48.2 | 80.85 | 29.9 | 750 | 789.4737 | 7.8947 | 3.9474 | 2559.11 | 100-240 | 10-35 | 10-80 | 2 | C14 | C13/C14 & C13/C20 | 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore | PowerStore X model(Gen1) | 1000_X | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1630 | - | 8.1 | 5449 | 240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 3000_X | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1630 | - | 8.1 | 5449 | 240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 5000_X | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1758 | 1793 | - | 9 | 5995 | 240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 7000_X | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1831 | 1869 | - | 9.3 | 6248 | 240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 9000_X | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 2047 | 2089 | - | 10.4 | 6985 | 240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore | PowerStore T model(Gen1) | 500_T | 2 | - | 8.72 | 44.72 | 79.55 | 37.4 | 1040 | 1061 | 10.6 | 5.3 | 3549 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 | C13/C14 & C13/C20 | 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 1000_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1630 | - | 8.1 | 5449 | 240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 3000_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1630 | - | 8.1 | 5995 | 240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 5000_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1758 | 1793 | - | 9 | 5995 | 240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 7000_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1831 | 1869 | - | 9.3 | 6248 | 240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 9000_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 2047 | 2089 | - | 10.4 | 6985 | 240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 25x2.5" DAE #1(SAS) | 2 | - | 8.64 | 44.45 | 33.02 | 20.23 | 432 | 485 | 4.5 | 2.4 | 1474 | 100-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 | diskフル搭載
PowerStore |  | 24x2.5" DAE #1(NVMe) | 2 | - | 8.89 | 43.18 | 65.3 | 33.5 | 965 | 1016 | 10.06 | 5 | 3293 | 100-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 | diskフル搭載
PowerStore | PowerStore T model(Gen2) | 500_T | 2 | - | 8.72 | 44.72 | 79.55 | 37.4 | 1040 | 1061 | 10.6 | 5.3 | 3549 | 100-240 | 5-35 | 20-80 | 2 | 100V:C20 200V:C14 | C13/C14 & C13/C20 | 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 1200_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1629.6 | - | 8.1 | 5449 | 200-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 3200_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1597 | 1629.6 | - | 8.1 | 5995 | 200-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 5200_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 1758 | 1792.9 | - | 9 | 5995 | 200-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 & C13/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 9200_T | 2 | - | 8.72 | 44.72 | 79.55 | 41.7 | 2047 | 2088.8 | - | 10.4 | 6985 | 200-240 | 5-35 | 20-80 | 2 | C20 | C19/C20 | Low Line voltages (110 – 120 volts) require the use of a step-up transformer 200V電源はC13/C14とC13/C20の2種がバンドル
PowerStore |  | 24x2.5" DAE #1(NVMe) | 2 | - | 8.89 | 43.18 | 65.3 | 33.5 | 965 | 1016 | 10.06 | 5 | 3293 | 100-240 | 5-35 | 20-80 | 2 | C14 | C13/C14 | diskフル搭載
PowerMax | PowerMax (EMC Rack)
PowerMax | PowerMax2000 (EMC Rack) | 1 system, 1 PowerBrick | 10 | - | 190 | 61 | 106.7 | 281 | 2146.2 | 2190 | - | 10.731 | 7450 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/2 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 1 system, 2 PowerBricks, or 2 systems, 1 PowerBrick each | 20 | - | 190 | 61 | 106.7 | 430.9 | 4292.4 | 4380 | - | 21.462 | 14900 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 systems, 2 PowerBricks in one system, 1 PowerBrick in other | 30 | - | 190 | 61 | 106.7 | 580 | 6438.6 | 6570 | - | 32.193 | 22350 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 systems, 2 PowerBricks each system | 40 | - | 190 | 61 | 106.7 | 730 | 8584.8 | 8760 | - | 42.924 | 29800 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | VAとBTUは26度以下での数値
PowerMax | PowerMax8000 (EMC Rack) | 1 PowerBricks (PowerBricks#1) | 40 | - | 190 | 61 | 119 | 365 | 2479.4 | 2530 | - | 12.397 | 8000 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 PowerBricks (PowerBricks#2) | 40 | - | 190 | 61 | 119 | 501 | 4753 | 4850 | - | 23.765 | 15400 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 3 PowerBricks (PowerBricks#3) | 40 | - | 190 | 61 | 119 | 643 | 7203 | 7350 | - | 36.015 | 23300 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 4 PowerBricks (PowerBricks#4) | 40 | - | 190 | 61 | 119 | 756 | 9182.6 | 9370 | - | 45.913 | 29700 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 1 PowerBricks (PowerBricks#5) | 40 | - | 190 | 61 | 119 | 301 | 2450 | 2500 | - | 12.25 | 7900 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 PowerBricks (PowerBricks#6) | 40 | - | 190 | 61 | 119 | 436 | 4429.6 | 4520 | - | 22.148 | 14300 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 3 PowerBricks (PowerBricks#7) | 40 | - | 190 | 61 | 119 | 579 | 6879.6 | 7020 | - | 34.398 | 22200 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 4 PowerBricks (PowerBricks#8) | 40 | - | 190 | 61 | 119 | 692 | 8859.2 | 9040 | - | 44.296 | 28600 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax | PowerMax (Customer Rack)
PowerMax | PowerMax2000 1-PowerBrick (Customer Rack) | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 636.02 | 649 | - | 3.1801 | 2170.1903 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 94 | 41 | 1694.42 | 1729 | - | 8.4721 | 5781.601 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax2000 2-PowerBrick (Customer Rack) | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 636.02 | 649 | - | 3.1801 | 2170.1903 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 94 | 41 | 1663.06 | 1697 | - | 8.3153 | 5674.5963 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 636.02 | 649 | - | 3.1801 | 2170.1903 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 94 | 41 | 1694.42 | 1729 | - | 8.4721 | 5781.601 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 1-PowerBrick (Customer Rack) | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 2-PowerBrick (Customer Rack) | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 3-PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 4-PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #4 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #6 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 5 -PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #5 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #8 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #7 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #4 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #6 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 6 -PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #6 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #9 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #5 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #8 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #7 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #4 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #6 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 7 -PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #7 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #11 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #10 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #6 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #9 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #5 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #8 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #7 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #4 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #6 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8000 8 -PowerBrick (Customer Rack) | Engine(512GB/1TB/2TB) #8 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #12 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #7 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #11 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #10 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #6 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #9 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #5 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #8 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #7 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #4 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #6 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(512GB/1TB/2TB) #3 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #5 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | 18 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | 18 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 501.5848 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14 | SPSから2本接続。
PowerMax |  | Engine(512GB/1TB/2TB) #2 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1783.6 | 1820 | - | 8.918 | 6085.8958 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Work tray | 1 | - | 4.4 | 48.3 | 43.2 | - | 98 | 100 | - | 0.49 | 334.3899 | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Ethernet Switch | 1 | - | 4.125 | 41.8 | 86.4 | 3.52 | 29.4 | 30 | - | 0.147 | 100.317 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | DELL X1018*2台/奥行はトレイ込みのサイズ
PowerMax |  | Engine(512GB/1TB/2TB) #1 | 4 | - | 17.78 | 48.3 | 104.2 | 41 | 1815.94 | 1853 | - | 9.0797 | 6196.2445 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.89 | 48.3 | 61 | 31 | 572.32 | 584 | - | 2.8616 | 1952.8369 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.89 | 48.3 | 61 | 31 | 667.38 | 681 | - | 3.3369 | 2277.1951 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax NX (EMC Rack)
PowerMax | PowerMax2500 (EMC Rack) | 1 system, 1 engine(1DAE) | 5 | - | 199.2 | 60 | 114.8 | 309.4 | 2168.74 | 2213 | - | 10.8437 | 7551 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/2 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 1 system, 2 engines(2DAEs) | 10 | - | 199.2 | 60 | 114.8 | 414.2 | 4337.48 | 4426 | - | 21.6874 | 15102 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 system, 1 engines(1DAE) | 10 | - | 199.2 | 60 | 114.8 | 414.2 | 4337.48 | 4426 | - | 21.6874 | 15102 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 3 system, 1 engines(1DAE) | 15 | - | 199.2 | 60 | 114.8 | 519 | 6506.22 | 6639 | - | 32.5311 | 22654 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 2 system, 4 engines(4DAEs) | 10 | - | 199.2 | 60 | 114.8 | 622.2 | 8674.96 | 8852 | - | 43.3748 | 30205 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | 3 systems, 6 engines(6DAEs) | 30 | - | 199.2 | 60 | 114.8 | 830.1 | 13012.44 | 13278 | - | 65.0622 | 45307 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/12 | - |  | VAとBTUは26度以下での数値
PowerMax | PowerMax8500 (EMC Rack) | System Bay 1: 1 engine, 1DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 390.963 | 3231.5598 | 3297.51 | - | 16.1578 | 11251.3 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 1 engine, 2DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 425.258 | 4075.0517 | 4158.216 | - | 20.3753 | 14188.08 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 2 engines, 1DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 445.835 | 4929.498 | 5030.1 | - | 24.6475 | 17163 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 2 engines, 2DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 486.989 | 5805.8532 | 5924.34 | - | 29.0293 | 20214.2 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 2 engines, 3DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 535 | 6627 | 6763 | - | 33.135 | 23075 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 2 engines, 4DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 569.3 | 7559 | 7713 | - | 37.795 | 26317 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 3 engines, 2DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 541.861 | 7449.0192 | 7601.04 | - | 37.2451 | 25935.2 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 3 engines, 3DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 583.015 | 8325.3744 | 8495.28 | - | 41.6269 | 28986.4 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 4 engines, 2DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 603.592 | 9201.7296 | 9389.52 | - | 46.0086 | 32037.6 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 4 engines, 3DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 644.746 | 10078.0848 | 10283.76 | - | 50.3904 | 35088.8 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 4 engines, 4DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 685.9 | 10954.44 | 11178 | - | 54.7722 | 38140 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 1engine, 1DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 300.8 | 2657.27 | 2711.5 | - | 13.2864 | 9251.75 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 1engine, 2DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 339.2 | 3613.8872 | 3687.64 | - | 18.0694 | 12582.38 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 2engines, 1DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 358.4 | 4570.5044 | 4663.78 | - | 22.8525 | 15913.01 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 2engines, 2DAE(balanced) | 42 | - | 199.2 | 60 | 120 | 390.4 | 5420.8308 | 5531.46 | - | 27.1042 | 18873.57 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 4 engines, 4DAEs(balanced) | 42 | - | 199.2 | 60 | 120 | 637.8 | 10629.08 | 10846 | - | 53.1454 | 37007 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/8 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 1: 6 engines, 4DAEs(dense) | 42 | - | 199.2 | 60 | 120 | 807.9 | 14601.02 | 14899 | - | 73.0051 | 50839 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/12 | - |  | VAとBTUは26度以下での数値
PowerMax |  | System Bay 2: 2 engines, 4DAEs(dense) | 42 | - | 199.2 | 60 | 120 | 516.7 | 6981.52 | 7124 | - | 34.9076 | 24308 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/12 | - |  | VAとBTUは26度以下での数値
PowerMax | PowerMax NX (Customer Rack)
PowerMax | PowerMax2500 2Nodes(1Node Pair) (Customer Rack) | 48 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は73.6
PowerMax |  | Engine(384GB/768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1452.911 | 1487.033 | - | 7.44 | 4957.5381 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は81.8
PowerMax | PowerMax2500 4Nodes(2Node Pair) (Customer Rack) | 48 DAE NVMe #2 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は73.6
PowerMax |  | Engine(384GB/768GB/1536GB) #2 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1452.911 | 1487.033 | - | 7.44 | 4957.5381 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は81.8
PowerMax |  | 48 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は73.6
PowerMax |  | Engine(384GB/768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1452.911 | 1487.033 | - | 7.44 | 4957.5381 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は81.8
PowerMax | PowerMax8500 2Nodes(1Node Pair) (Customer Rack) | Service tray | 1 | - | 4.4 | 48.3 | 43.2 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8500 4Nodes(2Node Pair) (Customer Rack) | Service tray | 1 | - | 4.4 | 48.3 | 43.2 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(768GB/1536GB) #2 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8500 6Nodes(3Node Pair) (Customer Rack) | Service tray | 1 | - | 4.4 | 48.3 | 43.2 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(768GB/1536GB) #3 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #2 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
PowerMax | PowerMax8500 8Nodes(4Node Pair) (Customer Rack) | Service tray | 1 | - | 4.4 | 48.3 | 43.2 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | 1 | C14 | C13/C14 | 幅、奥行き:space required by enclosures, engine rails, and cable management arms
PowerMax |  | Engine(768GB/1536GB) #4 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #3 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #2 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Engine(768GB/1536GB) #1 | 3 | - | 13.02 | 44.7 | 107.5 | 56 | 1837.499 | 1867.653 | - | 9.1875 | 6269.8068 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は76.2
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | Ethernet Switch | 1 | - | 4.32 | 42.8 | 68.58 | 12 | 332 | 332 | - | 1.66 | 1132.831 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
PowerMax |  | 24 DAE NVMe #1 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #2 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #3 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | 24 DAE NVMe #4 | 2 | - | 8.69 | 43.38 | 98.2 | 35 | 904.764 | 945.434 | - | 4.73 | 3087.1829 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | Full loaded 幅、奥行き:space required by enclosures, engine rails, and cable management arms/本体のみの奥行は50.8
PowerMax |  | SPS(2台) | 2 | - | 8.89 | 48.3 | 71.2 | 35 | 39.2 | 40 | - | 0.196 | 133.756 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14 | 幅:space required by enclosures, engine rails, and cable management arms
Symmetrix | VMAX AFA (EMC Rack)
Symmetrix | VMAX 250F/FX (EMC Rack) | 1 system, 1 V-Brick | - | - | 190 | 61 | 106.7 | 258 | 2058 | 2100 | - | 10.29 | 6271 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/2 | - |  | Engineの電源はSPS から2本接続。
Symmetrix |  | 1 system, 2 V-Bricks, or 2 systems, 1 V-Brick each | - | - | 190 | 61 | 106.7 | 385 | 4018 | 4100 | - | 20.09 | 12542 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/2 | - |  | Engineの電源はSPS から2本接続。
Symmetrix |  | 2 systems, 2 V-Bricks in one system, 1 Vbrick in other | - | - | 190 | 61 | 106.7 | 513 | 5978 | 6100 | - | 29.89 | 18813 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | Engineの電源はSPS から2本接続。
Symmetrix |  | 2 systems, 2 V-Bricks each system | - | - | 190 | 61 | 106.7 | 640 | 7938 | 8100 | - | 39.69 | 25084 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/4 | - |  | Engineの電源はSPS から2本接続。
Symmetrix | VMAX 450F/FX (2-VBrick) (EMC Rack) | System bay #1 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 6556.2 | 6690 | - | 32.781 | 29638 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix |  | System bay #2 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 6154.4 | 6280 | - | 30.772 | 27538 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix | VMAX 850F/FX (2-VBrick) (EMC Rack) | System bay #1 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 6801.2 | 6940 | - | 34.006 | 30638 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix |  | System bay #2 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 6360.2 | 6490 | - | 31.801 | 28338 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix | VMAX 950F/FX (2-VBrick) (EMC Rack) | System bay #1 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 7105 | 7250 | - | 35.525 | 24712 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix |  | System bay #2 (2-VBrick) | - | - | 190 | 61 | 119 | 844 | 6664 | 6800 | - | 33.32 | 23178 | 200-240 | 10-32 | 20-80 | 三相/2, 単相/6 | - |  | maximum weights(Includes front and rear doors.) Values at <26°C are reflective of more steady state maximum values during normal operation.
Symmetrix | VMAX AFA (Customer Rack)
Symmetrix | VMAX 250F/FX (1-VBrick) (Cusotmer Rack) | Engine #1 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1250 | 1275 | - | 6.38 | 4265 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。
Symmetrix |  | SPS(2台) | 2 | - | 8.89 | 44.45 | 71.1 | 27 |  |  | - |  |  | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #1 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #2 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix | VMAX 250F/FX (2-VBrick) (Cusotmer Rack) | Engine #1 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1250 | 1275 | - | 6.38 | 4265 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。
Symmetrix |  | SPS(2台) | 2 | - | 8.89 | 44.45 | 71.1 | 27 |  |  | - |  |  | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #1 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #2 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Engine #2 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1250 | 1275 | - | 6.38 | 4265 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Engineの電源はSPS から2本接続。
Symmetrix |  | SPS(2台) | 2 | - | 8.89 | 44.45 | 71.1 | 27 |  |  | - |  |  | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #3 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Direct DAE #4 | 2 | - | 8.89 | 44.7 | 33.02 | 20.23 | 435 | 500 | 4.73 | 2.5 | 1706 | 200-240 | 10-32 | 20-80 | 2 | C14 | C13/C14
Symmetrix | VMAX 950F/FX (1V-Brick-Full load) (Cusotmer Rack) | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14
Symmetrix |  | Engine #1 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1430.8 | 1460 | - | 6.38 | 4700 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Chassisは250Fと同一
Symmetrix |  | PDU *2 | 2 | - | 8.89 | 22.86 | 62.23 | 11.8 | - | - | - | - | - | 200-240 | 10-35 | 20-80 | 単相6/三相2 | - | - | 2PDU included
Symmetrix |  | KVM/1GBE Switch | 2 | - | - | - | - | 11 | 39.2 | 40 | - | - | 100 | - | - | - | -
Symmetrix |  | 2.5" x 120 DAE #1 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Vmax3と同一Chassis
Symmetrix |  | 2.5" x 120 DAE #2 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Vmax3と同一Chassis
Symmetrix | VMAX 950F/FX (2V-Brick-Full load) (Cusotmer Rack) | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | エンジン#1用
Symmetrix |  | 18 Port MIBE Switch#1 | - | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 500 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14
Symmetrix |  | 18 Port MIBE Switch#2 | - | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 500 | 200-240 | 10-35 | 20-80 | N/A | C14 | C13/C14
Symmetrix |  | Engine #1 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1430.8 | 1460 | - | 6.38 | 4700 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Chassisは250Fと同一
Symmetrix |  | PDU *2 | 2 | - | 8.89 | 22.86 | 62.23 | 11.8 | - | - | - | - | - | 200-240 | 10-35 | 20-80 | 単相6/三相2 | - | - | 2PDU included
Symmetrix |  | Engine #2 | 4 | - | 17.78 | 44.45 | 83.8 | 46 | 1430.8 | 1460 | - | 6.38 | 4700 | 200-240 | 10-32 | 20-80 | N/A | C14 | C13/C14 | Chassisは250Fと同一
Symmetrix |  | KVM/1GBE Switch | 2 | - | - | - | - | 11 | 39.2 | 40 | - | - | 100 | - | - | - | 2
Symmetrix |  | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | エンジン#2用
Symmetrix |  | 2.5" x 120 DAE #1 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14 | Vmax3と同一Chassis
Symmetrix |  | 2.5" x 120 DAE #2 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14
Symmetrix |  | 2.5" x 120 DAE #3 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14
Symmetrix |  | 2.5" x 120 DAE #4 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 1706 | 200-240 | 10-32 | 20-80 | 4 | C14 | C13/C14
Symmetrix |  | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | IB switch用
Symmetrix | VMAX 3 (EMC Rack)
Symmetrix | VMAX100K Single engine | System bay #1 | - | - | 190 | 61 | 119 | 937 | 10584 | 10800 | N / A | 52.92 | 35731 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix |  | System bay #2 | - | - | 190 | 61 | 119 | 937 | 10192 | 10400 | N / A | 50.96 | 34595 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX100K Dual engine | System bay #1 | - | - | 190 | 61 | 119 | 844 | 8624 | 8800 | N / A | 43.12 | 28715 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX200K Single engine | System bay #1 | - | - | 190 | 61 | 119 | 937 | 10682 | 10900 | N / A | 53.41 | 36398 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix |  | System bay #2 | - | - | 190 | 61 | 119 | 937 | 10388 | 10600 | N / A | 51.94 | 35262 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX200K Dual engine | System bay #1 | - | - | 190 | 61 | 119 | 844 | 8918 | 9100 | N / A | 44.59 | 30048 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix |  | System bay #2 | - | - | 190 | 61 | 119 | 844 | 8624 | 8800 | N / A | 43.12 | 28912 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX400K Single engine | System bay #1 | - | - | 190 | 61 | 119 | 937 | 10878 | 11100 | N / A | 54.39 | 36936 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix |  | System bay #2 | - | - | 190 | 61 | 119 | 937 | 10486 | 10700 | N / A | 52.43 | 35650 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX400K Dual engine | System bay #1 | - | - | 190 | 61 | 119 | 844 | 9212 | 9400 | N / A | 46.06 | 30975 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix |  | System bay #2 | - | - | 190 | 61 | 119 | 844 | 8820 | 9000 | N / A | 44.1 | 29688 | 200–240 | 10-35 | 20-80 | 三相/2, 単相/6 | -
Symmetrix | VMAX 3 (Customer Rack)
Symmetrix | VMAX3 100K (Dual Engine 2*DAE) ※Sample | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 1 |  | -
Symmetrix |  | 12 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 3 | 127.4 | 130 | N / A | 0.637 | 400 | 200-240 | 10-35 | 20-80 | 2 |  | -
Symmetrix |  | 12 Port MIBE Switch#2 | 1 | - | 4.4 | 44.45 | 71.1 | 3 | 127.4 | 130 | N / A | 0.637 | 400 | 200-240 | 10-35 | 20-80 | 2 |  | -
Symmetrix |  | Engine 100K(512GB/1TB) #1 | 4 | - | 17.78 | 44.45 | 83.8 | 53 | 989.8 | 1010 | N / A | 4.949 | 3100 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | PDU *2 | 2 | - | 8.89 | 22.86 | 62.23 | 11.8 | - | - | - | - | - | 200-240 | 10-35 | 20-80 | 単相6/三相2 |  | - | 2PDU included
Symmetrix |  | Engine 100K(512GB/1TB) #2 | 4 | - | 17.78 | 44.45 | 83.8 | 53 | 989.8 | 1010 | N / A | 4.949 | 3100 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | KVM | - | - | 4.4 | 44.45 | 53.34 | 11 | 39.2 | 40 | N / A | 0.196 | 100 | 200-240 | 10-35 | 20-80 | - |  | -
Symmetrix |  | Ethernet Switch 16 Port | 1 | - | 6.985 | 44.45 | 86.99 |  | 0 |  | N / A | 0 |  | 200-240 | 10-35 | 20-80 | 1 |  | - | Allied Telesis AT-GS900/16
Symmetrix |  | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 1 |  | -
Symmetrix |  | 2.5" x 120 DAE #1 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 3700 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | 2.5" x 120 DAE #2 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 3700 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix | VMAX3 Compornent | 2.2KW SPS | 2 | - | 8.89 | 44.45 | 71.1 | 26 | 294 | 300 | N / A | 1.47 | 1000 | 200-240 | 10-35 | 20-80 | 1 |  | -
Symmetrix |  | PDU *2 | 2 | - | 8.89 | 22.86 | 62.23 | 11.8 | - | - | - | - | - | 200-240 | 10-35 | 20-80 | 単相6/三相2 |  | - | 2PDU included
Symmetrix |  | KVM | - | - | 4.4 | 44.45 | 53.34 | 11 | 39.2 | 40 | N / A | 0.196 | 100 | 200-240 | 10-35 | 20-80 | - |  | -
Symmetrix |  | Ethernet Switch 16 Port | 1 | - | 6.985 | 44.45 | 86.99 |  | 0 |  | N / A | 0 |  | 200-240 | 10-35 | 20-80 | 1 |  | - | Allied Telesis AT-GS900/16
Symmetrix |  | 12 Port MIBE Switch#1 | 1 | - | 4.4 | 44.45 | 71.1 | 3 | 127.4 | 130 | N / A | 0.637 | 400 | 200-240 | 10-35 | 20-80 | 2 |  | -
Symmetrix |  | 18 Port MIBE Switch#1 | - | - | 4.4 | 44.45 | 71.1 | 10 | 147 | 150 | N / A | 0.735 | 500 | 200-240 | 10-35 | 20-80 | 2 |  | -
Symmetrix |  | Engine 100K(512GB/1TB) | 4 | - | 17.78 | 44.45 | 83.8 | 53 | 989.8 | 1010 | N / A | 4.949 | 3100 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | Engine 200K(512GB/1TB) | - | - | 17.78 | 44.45 | 83.8 | 53 | 1176 | 1200 | N / A | 5.88 | 3700 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | Engine 400K(512GB/1TB) | - | - | 17.78 | 44.45 | 83.8 | 54 | 1274 | 1300 | N / A | 6.37 | 4100 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | 2.5" x 120 DAE #1 | 3 | - | 13.2 | 44.7 | 87.63 | 56 | 1087.8 | 1110 | N / A | 5.439 | 3700 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
Symmetrix |  | 3.5” x 60 DAE #1 | - | - | 17.78 | 44.45 | 17.78 | 102 | 1146.6 | 1170 | N / A | 5.733 | 4000 | 200-240 | 10-35 | 20-80 | 4 |  | - | Full Loaded
XtremIO(X2-S) | XtremIO (X2-S) Virtual
XtremIO(X2-S) | XtremIO X2-S 1 X-Brick (Virtual XMS) | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 2 X-Bricks (Virtual XMS) | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 3 X-Bricks (Virtual XMS) | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 4 X-Bricks (Virtual XMS) | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 |  | - | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #7 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #8 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #4 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO (X2-S) Physical
XtremIO(X2-S) | XtremIO X2-S 1 X-Brick (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 2 X-Bricks (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-S) |  | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 3 X-Bricks (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) | XtremIO X2-S 4 X-Bricks (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-S) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | IBSW (12ports) #1 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | IBSW (12ports) #2 | 1 | - | 4.37 | 20 | 39.9 | 3.2 | 127.4 | 130 | - | 0.637 | 400 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Dingo 12ports
XtremIO(X2-S) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-S) |  | Storage Controller X2-S #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-S) |  | Storage Controller X2-S #7 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | Storage Controller X2-S #8 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 509.6 | 520 | - | 2.548 | 1700 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 384GB DIMMs
XtremIO(X2-S) |  | 2.5" DAE #4 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO (X2-T&R) Virtual
XtremIO(X2-T&R) | XtremIO X2-T 1 X-Brick (Virtual XMS) | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-T #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-T #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 40 | 372.4 | 380 | - | 1.862 | 1300 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(36 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 1 X-Brick (Virtual XMS) | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 2 X-Bricks (Virtual XMS) | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 3 X-Bricks (Virtual XMS) | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 4 X-Bricks (Virtual XMS) | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #7 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #8 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #4 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO (X2-T&R) Physical
XtremIO(X2-T&R) | XtremIO X2-T 1 X-Brick (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-T #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-T #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 40 | 372.4 | 380 | - | 1.862 | 1300 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(36 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 1 X-Brick (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 2 X-Bricks (PhysicalXMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-T&R) |  | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 3 X-Bricks (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) | XtremIO X2-R 4 X-Bricks (Physical XMS) | XtremIO Management Server | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 225.4 | 230 | - | 1.127 | 700 | - | 5-40 | 8-85 | 2 | C14 | C13/C14
XtremIO(X2-T&R) |  | 2.5" DAE #1 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #1 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #2 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #3 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #4 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #2 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | IBSW (36ports) #1 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | IBSW (36ports) #2 | 1 | - | 4.37 | 42.8 | 68.6 | 11.5 | 68.6 | 70 | - | 0.343 | 200 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Neptune 36ports
XtremIO(X2-T&R) |  | 2.5" DAE #3 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
XtremIO(X2-T&R) |  | Storage Controller X2-R #5 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #6 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Cable Management Duct | 1 | - | 4.32 | 43.8 | 91.44 | 0.78 | - | - | - | - | - | - | - | - | - |  | -
XtremIO(X2-T&R) |  | Storage Controller X2-R #7 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | Storage Controller X2-R #8 | 1 | - | 4.32 | 43.8 | 70.9 | 16 | 568.4 | 580 | - | 2.842 | 1900 | 90-264 | 5-40 | 8-85 | 2 | C14 | C13/C14 | 1024GB DIMMs
XtremIO(X2-T&R) |  | 2.5" DAE #4 | 2 | - | 8.89 | 43.8 | 92.7 | 48 | 519.4 | 530 | - | 2.597 | 1800 | 100-240 | 5-40 | 8-85 | 2 | C14 | C13/C14 | Full loaded(72 x SSDs)
VxRail | Vxrail
VxRail | VxRail E series | E560/F APPLIANCE | 1 | 1 | 4.28 | 43.4 | 73.4 | 21.9 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 3753.36 | 100-240 | 10-30 | 10-80 | 2 | C14 |  | R640 (2.5"x10HDD) / 定格:1100W
VxRail | VxRail S series | S570 APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 33.1 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 3753.36 | 100-240 | 10-25 | 10-80 | 2 | C14 |  | R740xd (2.5+3.5"HDD) / 定格:1100W
VxRail | VxRail P series VxRail V series | P&V570/F APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 3753.36 | 100-240 | 10-30 | 10-80 | 2 | C14 |  | R740 (2.5"HDD) / 定格:1100W
VxRail |  | P&V570/F APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 5459.43 | 200-240 | 10-30 | 10-80 | 2 | C14 | C13/C14 | R740 (2.5"HDD) / 定格:1600W
VxRail | VxRail V series | P&V570/F APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 2000 | 2105.2632 | 21.0526 | 10.5263 | 6824.28 | 200-240 | 10-30 | 10-80 | 2 | C20 | C19/C20 | R740 (2.5"HDD) / 定格:2000W
VxRail | VxRail G series | G560/F APPLIANCE | 2 | - | 8.68 | 44.8 | 79 | 41.46 | 2000 | 2105.2632 | 21.0526 | 10.5263 | 6824.28 | 220-240 | 10-30 | 10-80 | 2 | C20 | C19/C20 | 4node/chassis C6420 / 定格:2000W
VxRail |  | G560/F APPLIANCE | 2 | - | 8.68 | 44.8 | 79 | 41.46 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 8189.14 | 220-240 | 10-30 | 10-80 | 2 | C20 | C19/C20 | 4node/chassis C6420 / 定格:2400W
VxRail | (All-NVMe) VxRail E series | E560N APPLIANCE | 1 | 1 | 4.28 | 43.4 | 73.4 | 21.9 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 3753.36 | 100-240 | 10-30 | 10-80 | 2 | C14 |  | (2.5"x10NVMe) / 定格:1100W
VxRail |  | E560N APPLIANCE | 1 | 1 | 4.28 | 43.4 | 73.4 | 21.9 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 5459.43 | 200-240 | 10-30 | 10-80 | 2 | C14 | C13/C14 | (2.5"x10NVMe) / 定格:1600W
VxRail | (All-NVMe) VxRail P series | P580N APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 5459.43 | 200-240 | 10-30 | 10-80 | 2 | C14 | C13/C14 | (2.5" NVMe) / 定格:1600W
VxRail |  | P580N APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 2000 | 2105.2632 | 21.0526 | 10.5263 | 6824.28 | 200-240 | 10-30 | 10-80 | 2 | C20 | C19/C20 | (2.5" NVMe) / 定格:2000W
VxRail |  | P580N APPLIANCE | 2 | 1 | 8.68 | 43.4 | 67.8 | 28.1 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 8189.14 | 200-240 | 10-30 | 10-80 | 2 | C20 | C19/C20 | (2.5" NVMe) / 定格:2400W
VxRail | Vxrail D series | D560/F | 1 | 1 | 4.28 | 43.4 | 51.44 | 13 | 550 | 578.9474 | 5.7895 | 2.8947 | 2891 | 100-240 | 5-45 | 5-85 | 2 | C14 |  | 定格:550W
VxRail | Vxrail E series | E660/F/N | 1 | 1 | 4.28 | 43.4 | 78.7 | 21 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4299 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1100W ベゼルを含んだ奥行:+3.584cm
VxRail |  | E660/F/N | 1 | 1 | 4.28 | 43.4 | 78.7 | 21 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5459 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1400W ベゼルを含んだ奥行:+3.584cm
VxRail | Vxrail E series | E665/F | 1 | 1 | 4.28 | 43.4 | 65.73 | 16.75 | 550 | 578.9474 | 5.7895 | 2.8947 | 2107 | 110-240 | 10-35 | 8-80 | 2 | C14 |  | 定格:550W
VxRail |  | E665/F | 1 | 1 | 4.28 | 43.4 | 65.73 | 16.75 | 700 | 736.8421 | 7.3684 | 3.6842 | 2107 | 110-240 | 10-35 | 8-80 | 2 | C14 |  | 定格:700W
VxRail | Vxrail S series | S670 | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.3 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4299 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1100W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail |  | S670 | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.3 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5459 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1400W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail |  | S670 | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.3 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 9213 | 200-240 | 10-35 | 5-95 | 2 | C20 | C19/C20 | 定格：2400W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail | VxRail P series | P/V670/F | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.2 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4299 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1100W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail |  | P/V670/F | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.2 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5459 | 100-240 | 10-35 | 5-95 | 2 | C14 |  | 定格：1400W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail |  | P/V670/F | 2 | 1 | 8.68 | 43.4 | 73.4 | 35.2 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 9213 | 200-240 | 10-35 | 5-95 | 2 | C20 | C19/C20 | 定格：2400W AC mixed mode ベゼルを含んだ奥行:+3.584cm
VxRail | VxRail P series | P675N/F | 2 | 1 | 8.68 | 43.4 | 64.7 | 23.72 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 3753.36 | 100-240 | 10-35 | 8-85 | 2 | C14 |  | 定格:1100W
VxRail |  | P675N/F | 2 | 1 | 8.68 | 43.4 | 64.7 | 23.72 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 5459.43 | 200-240 | 10-35 | 8-85 | 2 | C14 | C13/C14 | 定格:1600W
VxRail | VxRail VD series | VD-4000R Chassis | 2 | - | 8.705 | 43.4 | 35.255 | 22.5 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4265 | 100-240 | -5-45 | - | 2 | C14 |  | 定格:1100W ベゼルを含んだ奥行:+10.25cm
VxRail |  | VD-4000R Chassis | 2 | - | 8.705 | 43.4 | 35.255 | 22.5 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5250 | 100-240 | -5-45 | - | 2 | C14 |  | 定格:1400W ベゼルを含んだ奥行:+10.25cm
VxRail |  | VD-4000Z Chassis | 2 | - | 8.705 | 43.4 | 35.5 | 12.16 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5250 | 100-240 | -5-55 | 8-80 | 2 | C14 |  | 定格:1400W ベゼルを含んだ奥行:+10cm
Connectrix | Brocade Switch
Connectrix | DS-300B | DS-300B #1 | 1 | - | 4.29 | 42.88 | 30.66 | 4.2 | 57 | 60 | 0.57 | 0.3 | 200 | 85-264 | 0-40 | 10-85 | 1 | C14
Connectrix | DS-6505B | DS-6505B #1 | 1 | - | 4.318 | 43.764 | 44.323 | 9.16 | 80 | 90 | 0.8 | 0.4 | 338 | 85-264 | 0-40 | 10-85 | 2 | C14 |  | コネクタ数は冗長電源オプション含む
Connectrix | DS-6510B | DS-6510B #1 | 1 | - | 4.318 | 43.764 | 44.323 | 9.16 | 107.8 | 110 | 1.078 | 0.6 | 400 | 85-264 | 0-40 | 10-85 | 2 | C14
Connectrix | DS-6520B | DS-6520B #1 | 2 | - | 8.674 | 42.925 | 60.975 | 16.92 | 464 | 488.4211 | 5 | 2.5 | 1582 | 85-264 | 0-40 | 10-85 | 2 | C14
Connectrix | DS-6610B | DS-6610B #1 | 1 | - | 4.29 | 42.88 | 30.6 | 5.76 | 77 | 81.0526 | 0.77 | 0.385 | 262.7349 | 90-264 | 0-55 | 5-95 | 1 | C14 |  | chassis includes one fixed power supply
Connectrix | DS-6620B | DS-6620B #1 | 1 | - | 4.39 | 44 | 35.56 | 7.73 | 206 | 216.8421 | 2.06 | 1.03 | 716 | 90-264 | 0-40 | 10-85 | 2 | C14
Connectrix | DS-6630B | DS-6630B #1 | 2 | - | 8.67 | 44 | 60.96 | 21.31 | 942 | 958.59 | 9.5 | 4.55 | 3215.12 | 90-264 | 0-40 | 10-90 | 2 | C14 |  | chassis includes one fixed power supply
Connectrix | DS-7720B | DS-7720B #1 | 1 | - | 4.39 | 44 | 35.56 | 7.17 | 349 | 367.3684 | 3.49 | 1.745 | 1192 | 90-264 | 0-40 | 10-85 | 2 | C14 |  | all 64 ports operating at 64G
Connectrix | DS-7730B | DS-7730B #1 | 2 | - | 8.67 | 44 | 60.96 | 21 | 969 | 1020 | 9.69 | 4.85 | 3306 | 100-240 | 0-40 | 10-85 | 2 | C14 |  | all 128 ports operating at 64G
Connectrix | Brocade MP-7800B | Brocade MP-7800B #1 | 1 | - | 4.5 | 43.2 | 64.1 | 10.9 | 147 | 150 | 1.47 | 0.7 | 590 | 85-264 | 0-40 | 10-85 | 2 | C14
Connectrix | Brocade MP-7810B | Brocade MP-7810B #1 | 1 | - | 4.4 | 44 | 45.7 | 8.35 | 132 | 146 | 1.29 | 0.65 | 449 | 90-264 | 0-40 | 10-90 | 2 | C14
Connectrix | Brocade MP-7840B | Brocade MP-7840B #1 | 2 | - | 8.64 | 44 | 60.9 | 20 | 492 | 517.8947 | 4.92 | 2.46 | 1679 | 90-264 | 0-40 | 10-85 | 2 | C14 |  | 消費電力(W): 長距離光トランシーバの場合
Connectrix | VDX-6740B | VDX-6740B #1 | 1 | - | 4.318 | 43.99 | 40.99 | 8.66 | 110 | 115.7895 | 1.1 | 0.55 | 1672.41 | 85-264 | 0-40 | 10-85 | 2 | C14
Connectrix | Brocade Switch (Director)
Connectrix | ED-DCX8510-4B | ED-DCX8510-4B #1 | 9 | - | 35.6 | 43.74 | 61.29 | 69 | 1176 | 1200 | 11.76 | 6 | 4182 | 85-264 | 0-40 | 5-93 | 2 | C20 | NEMAL6-20P | EMCでは100Vは要RPQ, C19-C20は標準搭載の2本分のみバンドル,汎用ラックだとL6-20がデフォルト(構成ガイドより)
Connectrix | ED-DCX8510-8B | ED-DCX8510-8B #1 | 14 | - | 62.23 | 43.74 | 61.29 | 103.38 | 1891.4 | 1930 | 18.914 | 9.7 | 7462 | 85-264 | 0-40 | 5-93 | 4 | C20 | NEMAL6-20P | EMCでは100Vは要RPQ, C19-C20は標準搭載の2本分のみバンドル,汎用ラックだとL6-20がデフォルト(構成ガイドより)
Connectrix | ED-DCX6-4B | DCX6-4B #1 | 9 | - | 40 | 43.74 | 61.29 | 68.95 | 2385 | 2510.5263 | 23.85 | 11.925 | 8139 | 85-264 | 0-40 | 5-93 | 2 | C20 | NEMAL6-20P | EMCでは200-240V対応,C19-C20仕様に変更したい場合は、RPQ申請と必要物品（電源ケーブル）が別途必要, EMCラックはEC-1700-Cへの搭載のみ可能(Bはサポートしてない)(構成ガイドより)
Connectrix | ED-DCX6-8B | DCX6-8B #1 | 14 | - | 61.23 | 43.74 | 61.04 | 145.8 | 4244 | 4467.3684 | 42.44 | 21.22 | 14485 | 85-264 | 0-40 | 5-93 | 4 | C20 | NEMAL6-20P | EMCでは200-240V対応,C19-C20仕様に変更したい場合は、RPQ申請と必要物品（電源ケーブル）が別途必要, EMCラックはEC-1700-Cへの搭載のみ可能(Bはサポートしてない)(構成ガイドより)
Connectrix | ED-DCX7-4B | ED-DCX7-4B#1 | 9 | - | 40 | 43.74 | 61.29 | 68.95 | 2264 | 2383.1579 | 22.64 | 11.32 | 10049 | 100-240 | 0-40 | 5-93 | 2 | C20 | NEMAL6-20P
Connectrix | ED-DCX7-8B | ED-DCX7-8B#1 | 14 | - | 61.23 | 43.74 | 61.04 | 145.8 | 4046 | 4258.9474 | 40.46 | 20.23 | 18362 | 100-240 | 0-40 | 5-93 | 4 | C20 | NEMAL6-20P
Connectrix | Cisco Switch
Connectrix | MDS-9148S | MDS-9148S #1 | 1 | - | 4.37 | 43.59 | 41.5 | 9 | 125.08 | 131.6632 | 1.2508 | 0.6254 | 426.7907 | 90-264 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9220i | MDS-9220i #1 | 1 | - | 4.37 | 43.94 | 51.1 | 9.8 | 283 | 297.8947 | 2.83 | 1.415 | 965.6361 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9250i | MDS-9250i #1 | 2 | - | 9.75 | 43.74 | 54.36 | 10.2 | 425 | 447.3684 | 4.25 | 2.125 | 1450.1602 | 100-240 | 0-40 | 10-90 | 3 | C14
Connectrix | MDS-9396S MDS-9396S-I | MDS-9396S #1 | 2 | - | 8.64 | 44.25 | 56.59 | 17.8 | 800 | 842.1053 | 8 | 4 | 2729.7133 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9132T | MDS-9132T #1 | 1 | - | 4.37 | 43.9 | 51.08 | 9.82 | 156 | 164.2105 | 1.56 | 0.78 | 532.2941 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9148T | MDS-9148T #1 | 1 | - | 4.37 | 43.9 | 55.6 | 8.5 | 297 | 312.6316 | 2.97 | 1.485 | 1013.4061 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9396T | MDS-9396T #1 | 2 | - | 8.61 | 44.25 | 56.59 | 18.88 | 555 | 584.2105 | 5.55 | 2.775 | 1893.7386 | 90-305 | 0-40 | 10-90 | 2 | C14 |  | Up to 96 ports.weight with fully configured.
Connectrix | MDS-9124V | MDS-9124V #1 | 1 | - | 4.37 | 43.94 | 45.72 | 8.5 | 146 | 153.6842 | 1.46 | 0.73 | 498.1727 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | MDS-9148V | MDS-9148V #1 | 1 | - | 4.37 | 43.94 | 45.72 | 9.8 | 286 | 301.0526 | 2.86 | 1.43 | 975.8725 | 100-240 | 0-40 | 10-90 | 2 | C14
Connectrix | Cisco Switch (Director)
Connectrix | MDS-9706 | MDS-9706 #1 | 9 | - | 39.62 | 43.9 | 81.3 | 147.4175 | 4360 | 4589.4737 | 43.6 | 21.8 | 14900 | 100-240 | 0-40 | 10-90 | 4 |  |  | EMCでは200-240V対応(Full Loaded)
Connectrix | MDS-9706-V2 | MDS-9706-V2 #1 | 9 | - | 39.62 | 43.9 | 81.3 | 147.4175 | 4360 | 4589.4737 | 43.6 | 21.8 | 14900 | 100-240 | 0-40 | 10-90 | 4 |  |  | EMCでは200-240V対応(Full Loaded)
Connectrix | MDS-9710 | MDS-9710 #1 | 14 | - | 61.9 | 43.9 | 86.4 | 191.6 | 8410 | 8852.6316 | 84.1 | 42.05 | 28700 | 100-240 | 0-40 | 10-90 | 6 |  | NEMAL6-20P | EMCでは200-240V対応(Full Loaded) HA構成の場合PowerSupply:8個
Connectrix | MDS-9710-V2 | MDS-9710-V2 #1 | 14 | - | 61.9 | 43.9 | 86.4 | 191.6 | 8410 | 8852.6316 | 84.1 | 42.05 | 28700 | 100-240 | 0-40 | 10-90 | 6 |  | NEMAL6-20P | EMCでは200-240V対応(Full Loaded) HA構成の場合PowerSupply:8個
Connectrix | MDS-9718 | MDS-9718 #1 | 26 | - | 114.9 | 43.9 | 88.9 | 334.18 | 16870 | 17757.8947 | 168.7 | 84.35 | 57600 | 100-240 | 0-40 | 10-90 | 12 |  | IEC60320 C19-20 | EC-1700非対応(Full Loaded) HA構成の場合PowerSupply:16個
Connectrix | MDS-9718-V3 | MDS-9718-V3 #1 | 26 | - | 114.9 | 43.9 | 88.9 | 334.18 | 16870 | 17757.8947 | 168.7 | 84.35 | 57600 | 100-240 | 0-40 | 10-90 | 12 |  | IEC60320 C19-20 | EC-1700非対応(Full Loaded) HA構成の場合PowerSupply:16個
Connectrix | Dell Switch
Connectrix | S3048-ON | S3048-ON #1 | 1 | - | 4.4 | 43.4 | 32 | 5.8 | 87 | 91.5789 | 0.87 | 0.435 | 296.86 | 100-240 | 0-45 | 95 | 2 | C14
Connectrix | S3124-ON | S3124-ON #1 | 1 | - | 4.4 | 43.4 | 43.5 | 6 | 54 | 56.8421 | 0.54 | 0.27 | 184.26 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | ※MAX消費電力、定格消費電力:200W コネクタ数は冗長電源オプション含む
Connectrix | S3124F-ON | S3124F-ON #1 | 1 | - | 4.4 | 43.4 | 43.5 | 6 | 67 | 70.5263 | 0.67 | 0.335 | 228.62 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | ※MAX消費電力、定格消費電力:200W コネクタ数は冗長電源オプション含む
Connectrix | S3148 | S3148 #1 | 1 | - | 4.35 | 43.4 | 40.7 | 6.3 | 65 | 68.4211 | 0.67 | 0.34 | 221.79 | 100-240 | 0-45 | 5-95 | 2 | C14
Connectrix | S4048-ON | S4048-ON #1 | 1 | - | 4.35 | 43.4 | 46 | 8.4 | 460 | 484.2105 | 4.6 | 2.3 | 1569.5852 | 100-240 | 0-45 | 10-85 | 2 | C14 |  | 消費電力は定格値
Connectrix | S4048T-ON | S4048T-ON #1 | 1 | - | 4.35 | 43.4 | 46 | 10.43 | 550 | 578.9474 | 5.5 | 2.75 | 1876.6779 | 100-240 | 0-45 | 10-85 | 2 | C14 |  | 消費電力は定格値
Connectrix | S4112T-ON (1Uに2台搭載) | S4112T-ON #1 | 1 | - | 4.125 | 20.9 | 45 | 3.81 | 200 | 210.5263 | 2.1053 | 1.0526 | 682.43 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix |  | S4112T-ON #2 |  | - |  | 20.9 |  | 3.81 | 200 | 210.5263 | 2.1053 | 1.0526 | 682.43 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix | S4112F-ON (1Uに2台搭載) | S4112F-ON #1 | 1 | - | 4.125 | 20.9 | 45 | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix |  | S4112F-ON #2 |  | - |  | 20.9 |  | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix | S4128F-ON | S4128F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 8.8 | 460 | 484.2105 | 4.6 | 2.3 | 890 | 100-240 | 0-45 | 10-85 | 2 | C14
Connectrix | S4128T-ON | S4128T-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.53 | 300 | 315.7895 | 3 | 1.5 | 1023 | 100-240 | 5-40 | 5-85 | 2 | C14
Connectrix | S4148F-ON | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
Connectrix | S4148T-ON | S4148T-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 10.33 | 440 | 463.1579 | 4.6316 | 2.3158 | 1500 | 100-240 | 5-40 | 5-85 | 2 | C14
Connectrix | S5048F-ON | S5048F-ON #1 | 1 | - | 4.35 | 43.4 | 45.7 | 9.98 | 750 | 789.4737 | 7.5 | 3.75 | 2559.11 | 100-240 | 0-45 | 10-85 | 2 | C14 |  | 定格消費電力
Connectrix | S5148F-ON | S5148F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 205.8 | 210 | 2.058 | 1.029 | 500 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
Connectrix | S5212F-ON (1Uに2台搭載) | S5212F-ON #1 | 1 | - | 4.1 | 20.9 | 49 | 3.6 | 337 | 354.7368 | 3.5474 | 1.7737 | 1149.9 | 100-239 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix |  | S5212F-ON #2 |  | - |  | 20.9 |  | 3.6 | 337 | 354.7368 | 3.5474 | 1.7737 | 1149.9 | 100-239 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Connectrix | S5224F-ON | S5224F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 533 | 561.0526 | 5.6105 | 2.8053 | 1818.68 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、定格750W
Connectrix | S5232F-ON | S5232F-ON #1 | 1 | - | 4.4 | 44.2 | 51.1 | 9.8 | 635 | 668.4211 | 6.6842 | 3.3421 | 2166.71 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、定格750W
Connectrix | S5248F-ON | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 647 | 681.0526 | 6.8105 | 3.4053 | 2207.66 | 100-240 | 5-45 | 5-90 | 2 | C14
Connectrix | S5296F-ON | S5296F-ON #1 | 2 | - | 8.7 | 44.2 | 51.1 | 15.1 | 893 | 940 | 9.4 | 4.7 | 3047.05 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、定格1100W
Connectrix | S5448F-ON | S5448F-ON #1 | 1 | - | 4.3 | 43.85 | 55 | 11.67 | 920 | 968.4211 | 9.6842 | 4.8421 | 3139.17 | 100-240 | 0-45 | 5-90 | 2 | C14 | C13/C14 | ※MAX消費電力、定格1600W
Connectrix | Z9264F-ON | Z9264F-ON #1 | 2 | - | 8.56 | 44.2 | 51 | 20 | 1104 | 1162.1053 | 11.04 | 5.52 | 3767.01 | 100-240 | 0-45 | 5-95 | 2 | C14
Connectrix | Z9432F-ON | Z9432F-ON #1 | 1 | - | 4.35 | 43.8 | 55 | 9.98 | 1404 | 1477.8947 | 14.04 | 7.02 | 4790.65 | 100-240 | 0-45 | 5-90 | 2 | C14 | C13/C14 | ※MAX消費電力、定格1600W
Connectrix | N1524 | N1524 #1 | 1 | - | 4.32 | 44 | 25.7 | 3 | 30.2 | 31.7895 | 0.302 | 0.151 | 103.1 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:40W
Connectrix | N1548 | N1548 #1 | 1 | - | 4.32 | 44 | 25.7 | 4 | 44.6 | 46.9474 | 0.446 | 0.223 | 152.2 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:100W
Connectrix | N2224X-ON | N2224X-ON #1 | 1 | - | 4.34 | 43.4 | 40 | 6.5 | 238 | 250.5263 | 2.38 | 1.19 | 812.09 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
Connectrix | N2248X-ON | N2248X-ON #1 | 1 | - | 4.34 | 43.4 | 40 | 6.9 | 326 | 343.1579 | 3.26 | 1.63 | 1112.36 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
Connectrix | N3224T-ON | N3224T-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.24 | 201 | 211.5789 | 2.01 | 1.005 | 685.85 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
Connectrix | N3224F-ON | N3224F-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.46 | 224 | 235.7895 | 2.24 | 1.12 | 764.32 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
Connectrix | N3248TE-ON | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
Connectrix | N3248X-ON | N3248X-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 7.3 | 480 | 505.2632 | 4.8 | 2.4 | 1637.83 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
PowerScale | PowerScale
PowerScale | F200 | F200 #1 | 1 | - | 4.28 | 43.4 | 80.85 | 21.9 | 249 | 262.1053 | 2.6211 | 1.3105 | 849.63 | 90-264 | 10-35 | 10-90 | 2 | C14 |  | Depth:end of the power supply latches
PowerScale | F600 | F600(2.2GHz)#1 | 1 | - | 4.28 | 43.4 | 80.85 | 21.9 | 497 | 523.1579 | 5.2316 | 2.6158 | 1695.84 | 90-264 | 10-35 | 10-90 | 2 | C14 |  | Depth:end of the power supply latches
PowerScale |  | F600(3.0GHz)#1 | 1 | - | 4.28 | 43.4 | 80.85 | 21.9 | 716 | 753.6842 | 7.5368 | 3.7684 | 2443.1 | 90-264 | 10-35 | 10-90 | 2 | C14 |  | Depth:end of the power supply latches
PowerScale | F900 | F900 #1 | 2 | - | 8.68 | 43.4 | 73.75 | 33.1 | 859 | 904.2105 | 9.0421 | 4.5211 | 2931.03 | 90-264 | 10-35 | 10-90 | 2 | C14 |  | Depth:end of the power supply latches
PowerScale | H700 | H700 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 118.4 | 1820 | 1870 | 18.7 | 9.35 | 6210.1 | 90-264 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
PowerScale |  | H700 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 64 | 910 | 940 | 9.4 | 4.7 | 3105.05 | 90-264 | 15-32 | 10-90 | 2 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
PowerScale | H7000 | H7000 4node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 141.4 | 1890 | 1940 | 19.4 | 9.7 | 6448.95 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth(front of bezel to rear 2.5” SSD cover ejector): 107.1 cm
PowerScale |  | H7000 2node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 78 | 940 | 970 | 9.7 | 4.85 | 3207.42 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth(front of bezel to rear 2.5” SSD cover ejector): 107.1 cm
PowerScale | A300 | A300 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 114.4 | 1270 | 1300 | 13 | 6.5 | 4333.42 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
PowerScale |  | A300 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 65 | 630 | 650 | 6.5 | 3.25 | 2149.65 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 4node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
PowerScale | A3000 | A3000 4node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 137.4 | 1330 | 1370 | 13.7 | 6.85 | 4538.15 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth: (front of bezel to rear 2.5” SSD cover ejector):107.1 cm
PowerScale |  | A3000 2node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 78 | 670 | 680 | 6.8 | 3.4 | 2286.14 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 4node/chassis Depth: (front of bezel to rear 2.5” SSD cover ejector):107.1 cm
PowerScale | P100 | P100 #1 | 1 | - | 4.28 | 43.4 | 80.85 | 21.9 | 464 | 488.4211 | 4.8842 | 2.4421 | 1583.24 | 100-240 | 10-35 |  | 2 | C14
PowerScale | B100 | B100 #1 | 1 | - | 4.28 | 43.4 | 80.85 | 21.9 | 474 | 498.9474 | 4.9895 | 2.4947 | 1617.36 | 100-240 | 10-35 |  | 2 | C14
PowerScale | S5232F-ON | S5232F-ON #1 | 1 | - | 4.4 | 44.2 | 51 | 9.8 | 635 | 668.4211 | 6.6842 | 3.3421 | 2166.71 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、定格750W
PowerScale | Z9100 | Dell Z9100 (32X40GbE) #1 | 1 | - | 4.4 | 43.4 | 46.2 | 8.62 | 606 | 637.8947 | 6.06 | 3.03 | 2067.7578 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | 32X40G or 128GX10G TOR for mixed or performance nodes.
PowerScale | Z9264 | Dell Z9264 (64X40GbE) #1 | 2 | - | 8.56 | 44.2 | 51 | 20 | 1104 | 1162.1053 | 11.04 | 5.52 | 3767.01 | 100-240 | 0-45 | 5-95 | 2 | C14
PowerScale | S4112F-ON (1Uに2台搭載) | S4112F-ON #1 | 1 | - | 4.125 | 20.9 | 45 | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
PowerScale |  | S4112F-ON #2 |  | - |  | 20.9 |  | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
PowerScale | S4148F-ON | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
PowerScale | InfiniBand SW | Mellanox 36port #1 | 1 | - | 4.36 | 42.8 | 68.58 | 10.8 | 208 | 218.9474 | 2.08 | 1.04 | 709.7255 | 100-240 | 0-45 | 10-85 | 2 | C14
PowerScale |  | Mellanox 36port(100Gb) #1 | 1 | - | 4.36 | 42.8 | 68.58 | 11 | 281 | 295.7895 | 4.5 | 2.9 | 958.8118 | 100-240 | 0-45 | 10-85 | 2 | C14 |  | SB7890
Isilon | Isilon Gen6
Isilon | F810 | F810 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 77.1 | 1830 | 1844 | 18.45 | 9.22 | 6200 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | F810 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 54.1 | 914 | 922 | 9.22 | 4.61 | 3100 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | F800 | F800 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 77.1 | 1693 | 1711 | 17.12 | 8.56 | 5800 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | F800 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 54.1 | 850 | 860 | 8.56 | 4.28 | 2900 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | H400 | H400 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 111.1 | 1103 | 1140 | 11.38 | 5.69 | 3800 | 90-264 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | H400 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 89.1 | 551 | 570 | 5.69 | 2.84 | 1900 | 90-264 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | H500 | H500 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 113.4 | 1640 | 1660 | 16.57 | 8.28 | 5600 | 90-264 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | H500 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 90.4 | 820 | 830 | 8.28 | 4.14 | 2800 | 90-264 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | H600 | H600 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 97.5 | 2180 | 2193 | 21.93 | 10.97 | 7400 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | H600 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 74.5 | 1090 | 1100 | 10.97 | 5.48 | 3700 | 90-265 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis ※100Vで使用時はTrancefomerが必要 Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | H5600 | H5600 4node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 130 | 2290 | 2300 | 23.01 | 11.5 | 7800 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis ※100Vで使用時はTrancefomerが必要 Depth(front of bezel to rear 2.5” SSD cover ejector): 107.1 cm
Isilon |  | H5600 2node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 80 | 1143 | 1150 | 11.5 | 5.75 | 3900 | 90-265 | 15-32 | 10-90 | 4 | C14 |  | 2node/chassis ※100Vで使用時はTrancefomerが必要 Depth(front of bezel to rear 2.5” SSD cover ejector): 107.1 cm
Isilon | A200 | A200 4node #1 | 4 | - | 17.8 | 44.8 | 91 | 108.9 | 1053 | 1090 | 10.87 | 5.44 | 3600 | 90-264 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon |  | A200 2node #1 | 4 | - | 17.8 | 44.8 | 91 | 86.9 | 530 | 544 | 5.44 | 2.72 | 1800 | 90-264 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis Depth (front of bezel to rear 2.5” SSD cover ejector): 95.5 cm
Isilon | A2000 | A2000 4node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 129.3 | 1300 | 1330 | 13.28 | 6.64 | 4400 | 90-264 | 15-32 | 10-90 | 4 | C14 |  | 4node/chassis Depth: (front of bezel to rear 2.5” SSD cover ejector):107.1 cm
Isilon |  | A2000 2node #1 | 4 | - | 17.8 | 44.8 | 102.6 | 105.3 | 650 | 665 | 6.64 | 3.32 | 2200 | 90-264 | 15-32 | 10-90 | 2 | C14 |  | 2node/chassis Depth: (front of bezel to rear 2.5” SSD cover ejector):107.1 cm
Isilon | Ethernet Switch | S5232F-ON #1 | 1 | - | 4.4 | 44.2 | 51 | 9.8 | 635 | 668.4211 | 6.6842 | 3.3421 | 2166.71 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | ※MAX消費電力、定格750W
Isilon | Ethernet Switch | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
Isilon | Ethernet Switch (1Uに2台搭載) | S4112F-ON #1 | 1 | - | 4.125 | 20.9 | 45 | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Isilon |  | S4112F-ON #2 |  | - |  | 20.9 |  | 3.81 | 180 | 189.4737 | 1.8947 | 0.94737 | 614.19 | 100-240 | 5-40 | 5-95 | 2 | C14 |  | ※MAX消費電力、1Uに2台搭載
Isilon | Ethernet Switch | Dell Z9100 (32X40GbE) #1 | 1 | - | 4.4 | 43.4 | 46.2 | 8.62 | 606 | 637.8947 | 6.06 | 3.03 | 2067.7578 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | 32X40G or 128GX10G TOR for mixed or performance nodes.
Isilon |  | Dell Z9264 (64X40GbE) #1 | 2 | - | 8.56 | 44.2 | 51 | 20 | 1600 | 1684.2105 | 16 | 8 | 5459.4266 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | 64X40G or 128X10G TOR for mixed or performance nodes.
Isilon |  | Celestica D2024(24port 10GbE, 2port 40GbE) #1 | 1 | - | 4.38 | 43.33 | 43.8 | 7.71 | 160 | 160 | 1.6 | 0.8 | 500 | 100-240 | 0-45 | 5-95 | 2 | C14
Isilon |  | Celestica D2060(48port 10GbE, 6port 40GbE) #1 | 1 | - | 4.4 | 43.33 | 52 | 9.98 | 210 | 210 | 2.1 | 1.05 | 700 | 100-240 | 0-45 | 5-95 | 2 | C14
Isilon |  | Celestica D4040(32port 40GbE; ) #1 | 1 | - | 4.38 | 43.38 | 52 | 9.98 | 320 | 320 | 3.2 | 1.6 | 1100 | 100-240 | 0-45 | 5-95 | 2 | C14 |  | supports 40 to 10GbE breakout cables
Isilon |  | Arista 7304 (96port 10GbE) #1 | 8 | - | 35.2 | 44.1 | 60.3 | 85.45 | 3000 | 3157.8947 | - | 15 | 10236.4249 | 200-240 | 0-40 | 5-95 | 4 | C20 | C19/C20 | DCS-7304/PS4搭載/電源ケーブルはバンドル(QAR/BOMに型番無) 標準で48port(48x 10GbE and 4x 40GbE)のline cardが2枚搭載。 最大line card搭載数は4、10Gportは最大512port(40G*4にbreakoutケーブル使用した場合)
Isilon |  | Arista 7308(64port 40GbE) #1 | 13 | - | 57.2 | 44.1 | 60.3 | 135.6 | 6000 | 6315.7895 | - | 30 | 20472.8498 | 200-240 | 0-40 | 5-95 | 6 | C20 | C19/C20 | 型番:851-0261/ PS6搭載/電源ケーブルはバンドル(QAR/BOMに型番無) 標準で32port(32x 40GbE ports)のline cardが2枚搭載。 最大line card搭載数は8、40Gportは最大256port,10Gportは最大1024port(40Gにbreakoutケーブル使用した場合)
Isilon | Transformer | POWERTRONIX ISOLATION STATION #1 | 2 | - | 8.81 | 40.13 | 43.94 | 29.94 | Not consume power |  | 30 | - | - | 100-120 | 5-40 | 0-95 | 1 | - | NEMAL6-30P | 1 per 2Node
Isilon | InfiniBand SW | Mellanox 36port #1 | 1 | - | 4.36 | 42.8 | 68.58 | 10.8 | 208 | 218.9474 | 2.08 | 1.04 | 709.7255 | 100-240 | 0-45 | 10-85 | 2 | C14
Isilon |  | Mellanox 36port(100Gb) #1 | 1 | - | 4.36 | 42.8 | 68.58 | 11 | 281 | 295.7895 | 4.5 | 2.9 | 958.8118 | 100-240 | 0-45 | 10-85 | 2 | C14 |  | SB7890
Isilon |  | Infinity Normal Chassis | 4 | - | 17.8 | 61 | 88.9 |  | - | - | - | - | - | - | - | -
Isilon |  | INFINITY Superior COMPUTE (Node Pair) | [17 empty] | 2Node pair
Isilon | Isilon Gen5
Isilon | InfiniBand SW | Mellanox 8port #1 | 1 | - | 4.4 | 20 | 25 | 1.92 | 66 | 69.4737 | 0.66 | 0.33 | 225 | 100-240 | 0-45 | 10-90 | 1
Isilon |  | Mellanox 18port #1 | 1 | - | 4.4 | 44 | 41 | 5.9 | 118.3 | 124.5263 | 1 | 0.5 | 402 | 100-240 | 0-45 | 10-90 | 1
Isilon |  | Mellanox 36port #1 | 1 | - | 4.36 | 42.8 | 68.58 | 10.8 | 208 | 218.9474 | 2.08 | 1.04 | 709.7255 | 100-240 | 0-45 | 10-85 | 2
Isilon |  | Qlogic 18port #1 | 1 | - | 4.32 | 43.96 | 36.25 | 6.8 | 100 | 105.2632 | 1 | 0.5 | 341 | 100-240 | 0-45 | 5-85 | 1
Isilon |  | Qlogic 36port #1 | 1 | - | 4.45 | 44 | 65.4 | 11.8 | 275 | 289.4737 | 3.6 | 1.3 | 938.3 | 90-264 | 5-40 | 10-85 | 2
Isilon |  | Qlogic (48-96port) #1 | 5 | - | 22.11 | 43.96 | 65 | 18.2 | 960 | 1010.5263 | 9.6 | 4.8 | 3277 | 100-240 | 0-40 | 5-85 | 4
Isilon |  | Mellanox (54 to108port) #1 | 7 | - | 30.95 | 48.26 | 68.58 | 82 | 1643 | 1729.4737 | 16.43 | 8.215 | 5606 | 220 | 0-45 | 10-85 | 2 |  |  | ・重量は最大搭載時。標準搭載は49.0kg ・-NRはPSUがN+N(PSU2)モデルのため、1670WのPSUを搭載 ・N+N redundancy ONLY works with a supply voltage of 220V. ・The switch platform uses 7U of rack space in a standard 19” rack, 6U for the chassis and 1U for the shelf.The shelf adds 44.5mm to the height ・WとBTU/hrはFDR Opticalの数値を採用
Isilon |  | Mellanox (54 to 216port) #1 | 10 | - | 44.45 | 48.26 | 68.58 | 147 | 3046 | 3206.3158 | 30.46 | 15.23 | 10393 | 220 | 0-45 | 10-85 | 4 |  |  | ・重量は最大搭載時。標準搭載は83.94kg ・-NRはPSUがN+N(PSU4)モデルのため、1670WのPSUを搭載 ・N+N redundancy ONLY works with a supply voltage of 220V.(P18) ・The switch platform uses 10U of rack space in a standard 19” rack, 9U for the chassisand 1U for the shelf.The shelf adds 44.5mm to the height ・WとBTU/hrはFDR Opticalの数値を採用
Isilon |  | Qlogic (48-144port)#1 | 10 | - | 44.47 | 43.96 | 65 | 41 | 2669 | 2809.4737 | 26.69 | 13.345 | 9108 | 100-240 | 0-40 | 5-85 | 4
Isilon | X series | X200 #1 | 2 | - | 8.8 | 48 | 72.4 | 27.7 | 680 | 715.7895 | 6.8 | 3.4 | 2350 | 100-240 | 15-32 | 5-95 | 2
Isilon |  | X210 #1 | 2 | - | 8.8 | 47.9 | 72.4 | 27.7 | 680 | 715.7895 | 6.8 | 3.4 | 2350 | 100-240 | 15-32 | 5-95 | 2
Isilon |  | X410 #1 | 4 | - | 17.7 | 48 | 72.4 | 54.5 | 750 | 789.4737 | 7.5 | 3.75 | 2600 | 100-240 | 15-32 | 5-95 | 2 |  |  | 100V/200V対応
Isilon |  | X410 #1 for LP | 4 | - | 17.7 | 48 | 72.4 | 54.5 | 750 | 789.4737 | 7.5 | 3.75 | 2600 | 100-240 | 15-32 | 5-95 | 2 |  |  | LP型番
Isilon | S series | S210 #1 | 2 | - | 8.8 | 48 | 77.47 | 25 | 500 | 526.3158 | 5 | 2.5 | 1700 | 100-240 | 15-32 | 40-55 | 2
Isilon | NL series | NL400 #1 | 4 | - | 17.7 | 48 | 79.4 | 57.7 | 850 | 894.7368 | 8.5 | 4.25 | 2900 | 100-240 | 15-32 | 5-95 | 2
Isilon | NL series | NL410 #1 | 4 | - | 17.7 | 48 | 79.4 | 51.7 | 850 | 894.7368 | 8.5 | 4.25 | 2900 | 100-240 | 15-32 | 5-95 | 2
Isilon | HD series | HD400 #1 | 4 | - | 17.7 | 48 | 88.9 | 100 | 1300 | 1368.4211 | N/A | 6.5 | 3750 | 200-240 | 15-32 | 5-95 | 2 |  | IEC320-C14
Isilon | Accelerator-A100 | Performance Accelerator #1 | 1 | - | 4.32 | 43.8 | 70.48 | 18.1 | 883 | 900 | 8.83 | 4.415 | 3015 | 100-240 | 10-35 | 20-80 | 2 |  |  | Width： without cabinet latch brackets
Isilon |  | Backup Accelerator #1 | 1 | - | 4.32 | 43.8 | 70.48 | 18.1 | 883 | 900 | 8.83 | 4.415 | 3015 | 100-240 | 10-35 | 20-80 | 2 |  |  | Width： without cabinet latch brackets
Isilon | InfiniBand SW | Mellanox IS5022 (8port) #1 | 1 | - | 4.4 | 20 | 25 | 1.92 | 66 | 69.4737 | 0.66 | 0.33 | 225 | 100-240 | 0-45 | 10-90 | 1
Isilon |  | Mellanox IS5023 QDR (18port) #1 | 1 | - | 4.4 | 44 | 41 | 5.9 | 118.3 | 124.5263 | 1 | 0.5 | 402 | 100-240 | 0-45 | 10-90 | 1
Isilon |  | Mellanox SX6790 QDR (36port) #1 | 1 | - | 4.36 | 42.8 | 68.58 | 10.8 | 208 | 218.9474 | 2.08 | 1.04 | 709.7255 | 100-240 | 0-45 | 10-85 | 2
Isilon |  | Qlogic 12200-18 (18port) #1 | 1 | - | 4.32 | 43.96 | 36.25 | 6.8 | 100 | 105.2632 | 1 | 0.5 | 341 | 100-240 | 0-45 | 5-85 | 1
Isilon |  | Qlogic 12300(36port) #1 | 1 | - | 4.45 | 44 | 65.4 | 11.8 | 275 | 289.4737 | 3.6 | 1.3 | 938.3 | 90-264 | 5-40 | 10-85 | 2
Isilon |  | Qlogic 12800-040 (48-96port) #1 | 5 | - | 22.11 | 43.96 | 65 | 18.2 | 960 | 1010.5263 | 9.6 | 4.8 | 3277 | 100-240 | 0-40 | 5-85 | 4
Isilon |  | Mellanox MSX6506-NR(54 to108port) #1 | 7 | - | 30.95 | 48.26 | 68.58 | 82 | 1643 | 1729.4737 | 16.43 | 8.215 | 5606 | 220 | 0-45 | 10-85 | 2 |  |  | ・重量は最大搭載時。標準搭載は49.0kg ・-NRはPSUがN+N(PSU2)モデルのため、1670WのPSUを搭載 ・N+N redundancy ONLY works with a supply voltage of 220V. ・The switch platform uses 7U of rack space in a standard 19” rack, 6U for the chassis and 1U for the shelf.The shelf adds 44.5mm to the height ・WとBTU/hrはFDR Opticalの数値を採用
Isilon |  | Mellanox MSX6512-NR(54 to 216port) #1 | 10 | - | 44.45 | 48.26 | 68.58 | 147 | 3046 | 3206.3158 | 30.46 | 15.23 | 10393 | 220 | 0-45 | 10-85 | 4 |  |  | ・重量は最大搭載時。標準搭載は83.94kg ・-NRはPSUがN+N(PSU4)モデルのため、1670WのPSUを搭載 ・N+N redundancy ONLY works with a supply voltage of 220V.(P18) ・The switch platform uses 10U of rack space in a standard 19” rack, 9U for the chassisand 1U for the shelf.The shelf adds 44.5mm to the height ・WとBTU/hrはFDR Opticalの数値を採用
Isilon |  | Qlogic 12800-120 (48-144port) #1 | 10 | - | 44.47 | 43.96 | 65 | 41 | 2669 | 2809.4737 | 26.69 | 13.345 | 9108 | 100-240 | 0-40 | 5-85 | 4
PowerProtect | PowerProtect DD
PowerProtect | PowerProtect DD3300 | DD3300 | 2 | - | 8.9 | 43.44 | 75.2 | 33.1 | 750 | 789.4737 | 7.5 | 3.75 | 2891 | 100-240 | 10-35 | 10-80 | 2 | C14
PowerProtect | PowerProtect DD6400 | DD6400 | 2 | - | 8.9 | 43.44 | 75.2 | 33.1 | 516 | 524 | 5.16 | 2.58 | 1760 | 100-240 | 10-35 | 10-80 | 2 | C14
PowerProtect | PowerProtect DD6900 | DD6900 | 2 | - | 8.9 | 43.44 | 75.2 | 33.1 | 352 | 364 | 3.52 | 1.76 | 1201 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | Cable Management Arm(CMA)が入る
PowerProtect |  | inc. CMA | 1 | - | 4.4 | - | - | - | - | - | - | - | - |  | - | - | - | - | -
PowerProtect | PowerProtect DD9400 | DD9400 | 2 | - | 8.9 | 43.44 | 75.2 | 33.1 | 635 | 647 | 6.35 | 3.175 | 2167 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | Cable Management Arm(CMA)が入る
PowerProtect |  | inc. CMA | 1 | - | 4.4 | - | - | - | - | - | - | - | - |  | - | - | - | - | -
PowerProtect | PowerProtect DD9900 | DD9900 | 3 | - | 13.21 | 43.44 | 81.3 | 49.9 | 1111 | 1117 | 11.11 | 5.555 | 3791 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | Cable Management Arm(CMA)が入る
PowerProtect |  | inc. CMA | 1 | - | 4.4 | - | - | - | - | - | - | - | - |  | - | - | - | - | -
PowerProtect | Expansion Shelves | FS25 #1 | 2 | - | 8.64 | 44.45 | 35.56 | 20.23 | 432 | 585 | 4.5 | 2.4 | 1474 | 100-240 | 10-35 | 20-80 | 2 | C14
PowerProtect |  | ES40 #1 | 3 | - | 13.34 | 44.75 | 35.6 | 30.8 | 281 | 313 | 2.9 | 1.6 | 959 | 100-240 | 10-35 | 20-80 | 2 | C14
PowerProtect |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 102 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DataDomain | Data Domain
DataDomain | DD6300 (7HDD) | DD6300 (7HDD) | 2 | - | 8.7 | 48.26 | 77.47 | 34 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain | DD6300 (12HDD) | DD6300 (12HDD) | 2 | - | 8.7 | 48.26 | 77.47 | 37.2 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain | DD6800 (4HDD+2SSD) | DD6800 (4HDD+2SSD) | 2 | - | 8.7 | 48.26 | 77.47 | 31 | 560 | 794 | 5.6 | 2.8 | 1910 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain | DD9300(4HDD+5SSD) | DD9300 (4HDD+5SSD) | 2 | - | 8.7 | 48.26 | 77.47 | 32.3 | 645 | 866 | 6.45 | 3.225 | 2200 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain | DD9800 (8SSD) | DD9800 (8SSD) | 4 | - | 17.3 | 48.26 | 70.36 | 51 | 1887 | 1981 | - | 9.435 | 6444 | 200-240 | 10-35 | 20-80 | 4 | C14 | C13/C14
DataDomain |  | FS15 shelf #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DD9800は自動構成
DataDomain | Expansion Shelves | ES30 #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 102 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DataDomain |  | FS15 shelf #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | ES30 for Cloud Tier #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | DS60 for Cloud Tier #1 | 5 | - | 22.23 | 44.45 | 92.46 | 102 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DataDomain | Data Domain HA
DataDomain | DD6800 HA構成 | DD6800 (4HDD+2SSD) #1 | 2 | - | 8.7 | 48.26 | 77.47 | 31 | 560 | 794 | 5.6 | 2.8 | 1910 | 200-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | DD6800 (4HDD+2SSD) #2 | 2 | - | 8.7 | 48.26 | 77.47 | 31 | 560 | 794 | 5.6 | 2.8 | 1910 | 200-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | FS15 shelf #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | HA構成時は必須
DataDomain | DD9300 HA構成 | DD9300 (4HDD+5SSD) #1 | 2 | - | 8.7 | 48.26 | 77.47 | 32.3 | 645 | 866 | 6.45 | 3.225 | 2200 | 200-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | DD9300 (4HDD+5SSD) #2 | 2 | - | 8.7 | 48.26 | 77.47 | 32.3 | 645 | 866 | 6.45 | 3.225 | 2200 | 200-240 | 10-35 | 20-80 | 2 | C14
DataDomain |  | FS15 shelf #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | HA構成時は必須
DataDomain | Expansion Shelves | ES30 (Retention) | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DataDomain | DD4200 (Extended Retention) | DD4200 ( Extended Retention) | 4 | - | 17.8 | 44.5 | 84 | 36.3 | 800 | 800 | - | 4 | 2730 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | EOL
DataDomain | DD4500 (Extended Retention) | DD4500 (Extended Retention) | 4 | - | 17.8 | 44.5 | 84 | 36.3 | 800 | 800 | - | 4 | 2730 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | EOL
DataDomain | DD6800 (4HDD+4SSD) (Extended Retention) | DD6800 (4HDD+4SSD) (Extended Retention) | 2 | - | 8.7 | 48.26 | 77.47 | 32 | 560 | 794 | 5.6 | 2.8 | 1910 | 200-240 | 10-35 | 20-80 | 2 | C14 |  | EOL
DataDomain | DD7200 (Extended Retention) | DD7200 (Extended Retention) | 4 | - | 17.8 | 44.5 | 84 | 36.3 | 800 | 800 | - | 4 | 2730 | 200-240 | 10-35 | 20-80 | 2 | C14 | C13/C14 | EOL
DataDomain | DD9300(4HDD+8SSD) (Extended Retention) | DD9300(4HDD+8SSD) (Extended Retention) | 2 | - | 8.7 | 48.26 | 77.47 | 34.5 | 645 | 866 | 6.45 | 3.225 | 2200 | 200-240 | 10-35 | 20-80 | 2 | C14 |  | EOL
DataDomain | DD9800 (15SSD) (Extended Retention) | DD9800 (15SSD) (Extended Retention) | 4 | - | 17.3 | 48.26 | 70.36 | 53.1 | 1887 | 1981 | - | 9.435 | 6444 | 200-240 | 10-35 | 20-80 | 4 | C14 | C13/C14 | EOL
DataDomain |  | F-15 SSD ES30 #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DD9800は自動構成
PowerProtect | PowerProtect DP
PowerProtect | PowerProtect DP 4400 | DP 4400 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 465.5 | 475 | 4.655 | 2.3275 | 1620 | 100-240 | 10-35 | 10-80 | 2 | C14
PowerProtect | PowerProtect DP 5900 | DP 5900 | 40 | - | 190.8 | 61.1 | 99.2 | 377.12 | 2773.4 | 2830 | - | 13.867 | 9300 | 200-240 | 10-35 | 20-80 | 2 | - | NEMAL6-30P | ラック込 Two power inlet connections for 3-phase. For rack 2, if required, two power inlet connections.
PowerProtect | PowerProtect DP 8400 | DP 8400 | 40 | - | 190.8 | 61.1 | 99.2 | 678.94 | 5370.4 | 5480 | - | 26.852 | 17800 | 200-240 | 10-35 | 20-80 | 4 | - | NEMAL6-30P | ラック込 Two power inlet connections for 3-phase. For rack 2, if required, two power inlet connections.
PowerProtect | PowerProtect DP 8900 | DP 8900 | 40 | - | 190.8 | 61.1 | 99.2 | 729.74 | 7105 | 7250 | - | 35.525 | 23400 | 200-240 | 10-35 | 20-80 | 4 | - | NEMAL6-30P | ラック込 Two power inlet connections for 3-phase. For rack 2, if required, two power inlet connections.
PowerProtect | NDMP Accelerator | Accelerator Node #1 | 2 | - | - | 48.26 | 87.7 | 29.5 | 239.12 | 244 | 2.44 | 1.22 | 737 | 100-240 | 10-35 | 20-80 | 2 | C14 | C13/C14
PowerProtect | Expansion Shelves | ES40 #1 | 3 | - | 13.34 | 44.75 | 35.6 | 30.8 | 281 | 313 | - | 1.6 | 959 | 100-240 | 10-35 | 20-80 | 2 | C14 | C13/C14
PowerProtect |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 102 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
PowerProtect | PowerProtect DM
PowerProtect | PowerProtect DM 5500 | DM 5500 | 2 | - | 8.68 | 44.8 | 81.03 | 43.2 | 932.96 | 952 | 9.3296 | 4.6648 | 4100 | 100-240 | 10-30 | 10-80 | 2 | C14
PowerProtect | PowerProtect X
PowerProtect | PowerProtect | X400 | 2 | - | 8.79 | 44.78 | 78.99 | 43.6 | 963 | 1013.6842 | 9.63 | 4.815 | 3286 | 100-240 | 10-35 | 10-80 | 2 |  |  | 1600W AC power supplies
PowerProtect |  | X400F | 2 | - | 8.68 | 43.4 | 71.55 | 33.07 | 667 | 702.1053 | 6.67 | 3.335 | 2276 | 100-240 | 10-35 | 10-80 | 2 |  |  | 1000W AC power supplies
PowerProtect |  | X400H | 2 | - | 8.68 | 43.4 | 71.55 | 33.07 | 667 | 702.1053 | 6.67 | 3.335 | 2276 | 100-240 | 10-35 | 10-80 | 2 |  |  | 1000W AC power supplies
IDPA | IDPA
IDPA | IDPA | IDPA 4400 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 465.5 | 475 | 4.655 | 2.3275 | 1620 | 100-240 | 10-35 | 10-80 | 2 | C14
IDPA | IDPA | IDPA 5300 | 40 | - | 190.5 | 60.96 | 100.08 | 277 | 1714.02 | 1749 | - | 8.5701 | 5800 | 100-240 | 10-35 | 20-80 | 4 |  | NEMAL6-30P | ラック込 ※接続コネクタ数は差構成によって、2もしくは4となります。
IDPA |  | IDPA 5800 | 40 | - | 190.8 | 61.1 | 99.2 | 377.12 | 1949.22 | 1989 | - | 9.7461 | 5935 | 100-240 | 10-35 | 20-80 | 4 |  | NEMAL6-30P | ラック込 ※接続コネクタ数は差構成によって、2もしくは4となります。
IDPA |  | IDPA 8300 | 40 | - | 190.8 | 61.1 | 99.2 | 678.94 | 3054.66 | 3117 | - | 15.2733 | 9479 | 100-240 | 10-35 | 20-80 | 4 |  | NEMAL6-30P | ラック込 *DP8300 with CT and NDMP options require two racks ※※接続コネクタ数は差構成によって、2もしくは4となります。
IDPA |  | IDPA 8800 | 40 | - | 190.8 | 61.1 | 99.2 | 729.74 | 3787.7 | 3865 | - | 18.9385 | 14243 | 200-240 | 10-35 | 20-80 | 4 |  | NEMAL6-30P | 2ラック込 ※接続コネクタ数は差構成によって、2もしくは4となります。
IDPA | Expansion Shelves | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 102 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA_DP5300 (Minimum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | DD6300-48TB | 2 | - | 8.7 | 48.26 | 77.47 | 37 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA | IDPA_DP5300 (Maximum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | a | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | Accelerator Gen4T Node #1 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DD6300-48TB | 2 | - | 8.7 | 48.26 | 77.47 | 37 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA_DP5800 (Minimum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | DD6800-16TB | 2 | - | 8.7 | 48.26 | 77.47 | 32 | 568.4 | 580 | 5.684 | 2.842 | 1900 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA_DP5800 (Maximum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | Accelerator Gen4T Node #1 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | Accelerator Gen4T Node #2 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | ES30-60S #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | ES30-60S #2 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | Accelerator Gen4T Node #3 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DD6800-16TB | 2 | - | 8.7 | 48.26 | 77.47 | 32 | 568.4 | 580 | 5.684 | 2.842 | 1900 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA |  | DS60 #2 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA 8300 (Minimum) ここまで完成 | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | 24-Port Ethernet Switch (2台) | 3 | - | 8.68 | 44.3 | 24 | 22 | 176.4 | 180 | 1.764 | 0.9 | 200 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | M1200 Storage Node #1 | 2 | - | - | 48.26 | 87.7 | 32 | 264.6 | 270 | 2.73 | 1.37 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | M1200 Storage Node #2 | 2 | - | - | 48.26 | 87.7 | 32 | 264.6 | 270 | 2.73 | 1.37 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | M1200 Storage Node #3 | 2 | - | - | 48.26 | 87.7 | 32 | 264.6 | 270 | 2.73 | 1.37 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | Utility Node | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.37 | 1.19 | 700 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | DD9300 (4HDD+5SSD) | 2 | - | 8.7 | 48.26 | 77.47 | 33 | 656.6 | 670 | 6.566 | 3.283 | 2200 | 200-240 | 10-35 | 20-80 | 2
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA 8300 (Maximum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | Accelerator Gen4T Node #1 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DD6800-48TB | 2 | - | 8.7 | 48.26 | 77.47 | 37 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA_DP5800 (Minimum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | DD6800-16TB | 2 | - | 8.7 | 48.26 | 77.47 | 32 | 568.4 | 580 | 5.684 | 2.842 | 1900 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA |  | DS60 #2 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA | IDPA_DP5800 (Maximum) | システム一式 | 40 | - | 190.5 | 60.96 | 100.08 | 181 | - | - | - | - | - | - | - | - | 2 |  | NEMAL6-30P | 40U-P Rack
IDPA |  | Accelerator Gen4T Node #1 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | Accelerator Gen4T Node #2 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | ES30-60S #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | ES30-60S #2 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
IDPA |  | DELL S4048-ON | 1 | - | 4.35 | 43.4 | 43.5 | 8 | 225.4 | 230 | 2.344 | 1.145 | 800 | 100-240 | 0-45 | 10-85 | - |  | IEC320-C14
IDPA |  | IDPA Compute R630 #1 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #2 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | IDPA Compute R630 #3 | 1 | - | 4.28 | 48.23 | 75.51 | 17 | 313.6 | 320 | 3.136 | 1.568 | 1100 | - | - | - | - |  | IEC320-C14 | 24 x 1.8" and 10 x 2.5" drive configuration
IDPA |  | Accelerator Gen4T Node #3 | 2 | - | - | 48.26 | 87.7 | 29 | 235.2 | 240 | 2.44 | 1.22 | 700 | 100-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DD6800-16TB | 2 | - | 8.7 | 48.26 | 77.47 | 32 | 568.4 | 580 | 5.684 | 2.842 | 1900 | 200-240 | 10-35 | 20-80 | - |  | IEC320-C14
IDPA |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA |  | DS60 #2 | 5 | - | 22.23 | 44.45 | 92.46 | 108 | 980 | 1000 | - | 4.9 | 3100 | 200-240 | 5-40 | 20-80 | - |  | IEC320-C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
IDPA |  | 24-Port Ethernet Switch | 1 | - | 4.43 | 44.3 | 24 | 6.88 | 88.2 | 90 | 0.9 | 0.375 | 100 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
IDPA |  | 24-Port Ethernet Switch (2台) | 3 | - | 8.68 | 44.3 | 24 | 6.88 | 88.2 | 90 | 0.882 | 0.45 | 100 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
Avamar | Avamar
Avamar | ADS Gen4T M600 | Utility Node | 2 | - | - | 48.26 | 87.7 | 29.5 | 232.26 | 237 | 2.37 | 1.19 | 716 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Internal Switch (2個分) | 3 | - | 8.68 | 44.3 | 24 | 6.88 | 24 | 90 | 0.9 | 0.375 | 82 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
Avamar |  | Internal Switch (2個分) | 3 | - | 8.8 | 43.2 | 25.4 | 6.2 | 39.2 | 40 | 0.392 | 0.196 | 100 | 110-240 | 0-45 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Dell switch N1124-T ON
Avamar |  | Storage Node (spare) | 2 | - | - | 48.26 | 87.7 | 30.9 | 249.9 | 255 | 2.55 | 1.28 | 781 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Storage Node #1 | 2 | - | - | 48.26 | 87.7 | 30.9 | 249.9 | 255 | 2.55 | 1.28 | 781 | 100-240 | 10-35 | 20-80 | 2
Avamar | ADS Gen4T M1200 | Utility Node | 2 | - | - | 48.26 | 87.7 | 29.5 | 232.26 | 237 | 2.37 | 1.19 | 716 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Internal Switch (2個分) | 3 | - | 8.68 | 44.3 | 24 | 6.88 | 24 | 90 | 0.9 | 0.375 | 82 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
Avamar |  | Internal Switch (2個分) | 3 | - | 8.8 | 43.2 | 25.4 | 6.2 | 39.2 | 40 | 0.392 | 0.196 | 100 | 110-240 | 0-45 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Dell switch N1124-T ON
Avamar |  | Storage Node (spare) | 2 | - | - | 48.26 | 87.7 | 32.3 | 267.54 | 273 | 2.73 | 1.37 | 846 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Storage Node #1 | 2 | - | - | 48.26 | 87.7 | 32.3 | 267.54 | 273 | 2.73 | 1.37 | 846 | 100-240 | 10-35 | 20-80 | 2
Avamar | ADS Gen4T M2400 | Utility Node | 2 | - | - | 48.26 | 87.7 | 29.5 | 232.26 | 237 | 2.37 | 1.19 | 716 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Internal Switch (2個分) | 3 | - | 8.68 | 44.3 | 24 | 6.88 | 24 | 90 | 0.9 | 0.375 | 82 | 100-240 | 0-55 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Brocade ICX6430-24 1Gb Ethernet Switch
Avamar |  | Internal Switch (2個分) | 3 | - | 8.8 | 43.2 | 25.4 | 6.2 | 39.2 | 40 | 0.392 | 0.196 | 100 | 110-240 | 0-45 | 5-95 | 2 |  |  | 配線スペース1Uを含む モデル：Dell switch N1124-T ON
Avamar |  | Storage Node (spare) | 2 | - | - | 48.26 | 87.7 | 36.4 | 327.32 | 334 | 3.34 | 1.67 | 1061 | 100-240 | 10-35 | 20-80 | 2
Avamar |  | Storage Node #1 | 2 | - | - | 48.26 | 87.7 | 36.4 | 327.32 | 334 | 3.34 | 1.67 | 1061 | 100-240 | 10-35 | 20-80 | 2
Avamar | ADS Gen4T S2400 Business Edition | Storage Node #1 (Single node only) | 2 | - | - | 48.26 | 87.7 | 50.5 | 290.08 | 296 | 2.96 | 1.48 | 928 | 100-240 | 10-35 | 20-80 | 2 |  |  | シングルノード専用モデル
Avamar | ADS Gen4T | Accelerator Node #1 | 2 | - | - | 48.26 | 87.7 | 29.5 | 239.12 | 244 | 2.44 | 1.22 | 737 | 100-240 | 10-35 | 20-80 | 2 | C14
Avamar | ADS Gen5A M25 | Utility Node | 2 | - | 8.89 | 43.43 | 75.18 | 33 | 492 | 508 | 5.08 | 2.54 | 1679 | 100-240 | 10-35 | 20-80 | 2 | C14
Avamar |  | S4128F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 8.8 | 460 | 484.2105 | 4.6 | 2.3 | 890 | 100-240 | 0-45 | 10-85 | 2 | C14
Avamar |  | S4128F-ON #2 | 1 | - | 4.4 | 43.1 | 45.7 | 8.8 | 460 | 484.2105 | 4.6 | 2.3 | 890 | 100-240 | 0-45 | 10-85 | 2 | C14
Avamar |  | Storage Node (spare) | 2 | - | 8.89 | 43.43 | 75.18 | 33 | 492 | 508 | 5.08 | 2.54 | 1679 | 100-240 | 10-35 | 20-80 | 2 | C14
Avamar |  | Storage Node #1 | 2 | - | 8.89 | 43.43 | 75.18 | 33 | 492 | 508 | 5.08 | 2.54 | 1679 | 100-240 | 10-35 | 20-80 | 2 | C14
Avamar | ADS Gen5A M25(Single Node) | Storage Node #1 | 2 | - | 8.89 | 43.43 | 75.18 | 33 | 492 | 508 | 5.08 | 2.54 | 1679 | 100-240 | 10-35 | 20-80 | 2 | C14
Avamar | ADS Gen5A Accelerator Node | Accelerator Node #1 | 2 | - | 8.89 | 43.43 | 75.18 | 33 | 511 | 528 | 5.28 | 2.64 | 1744 | 100-240 | 10-35 | 20-80 | 2 | C14
ECS | ECS (EX series)
ECS | EX300 | Switch S5148F-ON FE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5148F-ON FE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Service tray ※EMC rack only | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
ECS |  | Switch S5148F-ON FE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5148F-ON FE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | EX300_12TB-192TB #1 | 2 | - | 8.68 | 48.2 | 75.15 | 33 | 280 | 330 | 3.25 | 1.63 | 900 | 90-264 | 5-32 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm Based on R740xd 200V powercable is bundled
ECS | EX500 | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Service tray ※EMC rack only | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
ECS |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | EX500_12disk #1 | 2 | - | 8.68 | 48.2 | 88.1 | 32 | 545 | 580 | 5.8 | 2.9 | 1900 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は81.0cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm Based on R740xd 200V powercable is bundled
ECS |  | EX500_24disk #1 | 2 | - | 8.68 | 48.2 | 88.1 | 43 | 690 | 720 | 7.2 | 3.6 | 2400 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は81.0cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm Based on R740xd 200V powercable is bundled
ECS | EXF900 | Switch S5248F-ON FE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5248F-ON FE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Service tray ※EMC rack only | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
ECS |  | Switch S5248F-ON BE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5248F-ON BE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | EXF900 48TB 3.84TB*12 #1 | 2 | - | 8.68 | 48.2 | 75.1 | 22 | 692.41 | 711.72 | 7.12 | 3.56 | 2363 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS |  | EXF900 96TB 7.68TB*12#1 | 2 | - | 8.68 | 48.2 | 75.1 | 22 | 731.3 | 750.14 | 7.5 | 3.75 | 2495 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS |  | EXF900 192TB 15.36TB*12#1 | 2 | - | 8.68 | 48.2 | 75.1 | 22 | 742 | 750 | 7.5 | 3.75 | 2532 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS |  | EXF900 96TB 3.84TB*24#1 | 2 | - | 8.68 | 48.2 | 75.1 | 24 | 849 | 856.81 | 8.57 | 4.28 | 2897 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS |  | EXF900 192TB 7.68TB*24#1 | 2 | - | 8.68 | 48.2 | 75.1 | 24 | 860.4 | 867.53 | 8.68 | 4.34 | 2936 | 90-264 | 5-30 | 20-80 | 2 | C14 |  | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS |  | EXF900 384TB 15.36TB*24#1 | 2 | - | 8.68 | 48.2 | 75.1 | 24 | 851 | 861 | 8.61 | 4.31 | 2904 | 90-264 | 5-30 | 20-80 | 2 | C14 | C13/C14 | ※partsなしの奥行は67.8cm ※+3.6cmはベゼル込みの追加奥行、ベゼルなしだとこれが+2.2cm
ECS | EX3000 | Switch S5148F-ON FE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5148F-ON FE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5148F-ON BE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5148F-ON BE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.97 | 470 | 494.7368 | 4.7 | 2.35 | 1603.71 | 100-240 | 0-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Service tray ※EMC rack only | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
ECS |  | PDU#1 ※Quote check | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 |  | IEC320-C14
ECS |  | S_540_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 79 | 790 | 810 | 8.1 | 4.05 | 2700 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | S_720_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 95 | 940 | 960 | 9.6 | 4.8 | 3200 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | S_1080_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 128 | 1240 | 1260 | 12.6 | 6.3 | 4200 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | D_720_dual node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 101 | 1020 | 1050 | 10.5 | 5.25 | 3500 | 200-240 | 5-32 | 20-80 | 4 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | D_1080_dual node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 134 | 1320 | 1350 | 13.5 | 6.75 | 4500 | 200-240 | 5-32 | 20-80 | 4 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS | EX3000_16TB | S_720_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 79 | 790 | 810 | 8.1 | 4.05 | 2700 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | S_960_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 95 | 940 | 960 | 9.6 | 4.8 | 3200 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | S_1440_single node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 128 | 1240 | 1260 | 12.6 | 6.3 | 4200 | 200-240 | 5-32 | 20-80 | 2 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | D_960_dual node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 101 | 1020 | 1050 | 10.5 | 5.25 | 3500 | 200-240 | 5-32 | 20-80 | 4 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS |  | D_1440_dual node #1 | 4 | - | 17.38 | 48.24 | 124.268 | 134 | 1320 | 1350 | 13.5 | 6.75 | 4500 | 200-240 | 5-32 | 20-80 | 4 | C14 | C13/C14 | 本体の奥行は109.8cmだが、ケーブルまわりなどを加味してラックには奥行が120cm必要
ECS | EX5000 | Switch S5248F-ON FE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5248F-ON FE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5248F-ON BE#1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Switch S5248F-ON BE#2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 | C14 |  | 200V powercable is bundled
ECS |  | Service tray ※EMC rack only | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
ECS |  | S_25disk_single node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 69 | 1000 | 1008 | 10.08 | 5.04 | 3412 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS |  | S_50disk_single node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 90 | 1220 | 1227 | 12.27 | 6.14 | 4163 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS |  | S_75disk_single node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 111 | 1452 | 1460 | 14.6 | 7.3 | 4954 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS |  | S_100disk_single node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 132 | 1758 | 1763 | 17.63 | 8.82 | 5998 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS |  | D_50disk_dual node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 91 | 1795 | 1802 | 18.02 | 9.01 | 6125 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS |  | D_100disk_dual node #1 | 5 | - | 22.23 | 44.81 | 98.09 | 133 | 2254 | 2262 | 22.62 | 11.31 | 7691 | 200-240 | 5-32 | 20-80 | 2 | C20 | C19/C20 | 2400W, 200V powercable is bundled
ECS | ECS (D series)
ECS | D4600 D5600 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.64 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.64 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 640 | 673.6842 | 6.4 | 3.2 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 640 | 673.6842 | 6.4 | 3.2 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2 |  |  | Each 70 Dense DAE included 8 or 10TB-70 drives
ECS |  | DAE #2 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #3 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #4 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #5 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #6 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #7 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #8 | 4 | - | 17.7 | 44.9 | 100 | 82 | 862.4 | 880 | 8.624 | 4.312 | 2900 | 200-240 | 5-35 | 8-90 | 2
ECS | D6200 D7800 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.64 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.64 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 640 | 673.6842 | 6.4 | 3.2 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 640 | 673.6842 | 6.4 | 3.2 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2 |  |  | Each 98 Dense DAE included 8 or 10TB-98 drives
ECS |  | DAE #2 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #3 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #4 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #5 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #6 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #7 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS |  | DAE #8 | 4 | - | 17.7 | 44.9 | 100 | 97 | 1127 | 1150 | 11.27 | 5.635 | 3900 | 200-240 | 5-35 | 8-90 | 2
ECS | ECS (U series)
ECS | U400 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-10 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS | U400E | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-10 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS | U480E | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-10 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #6 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS | U400-T | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-10 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #6 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #7 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #8 | 4 | - | 17.78 | 45 | 87.63 | 48 | 539 | 550 | 5.39 | 2.695 | 1800 | 200-240 | 5-35 | 8-90 | 4
ECS | U2000 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-30 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #6 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #7 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #8 | 4 | - | 17.78 | 45 | 87.63 | 69 | 774.2 | 790 | 7.742 | 3.871 | 2700 | 200-240 | 5-35 | 8-90 | 4
ECS | U2800 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-45 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #6 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #7 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #8 | 4 | - | 17.78 | 45 | 87.63 | 86 | 960.4 | 980 | 9.604 | 4.802 | 3300 | 200-240 | 5-35 | 8-90 | 4
ECS | U4000 | Arista 7010T (1GbE) #1 | 1 | - | 4.4 | 44.5 | 25.4 | 4.3 | 65 | 68.4211 | 0.65 | 0.325 | 510 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Arista 7050SX (10GbE) #1 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2 |  |  | BOM確認済み:7050SX-64
ECS |  | Arista 7050SX (10GbE) #2 | 1 | - | 4.4 | 48.3 | 40.6 | 8.6 | 220 | 231.5789 | 2.2 | 1.1 | 750.6712 | 100-240 | 0-40 | 5-95 | 2
ECS |  | Server #1 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2 |  |  | (Gen2)Rinjin16-server
ECS |  | Server #2 | 2 | - | 8.79 | 43.8 | 73.3 | 38 | 627.2 | 640 | 6.272 | 3.136 | 2100 | 90-264 | 10-35 | 20-80 | 2
ECS |  | DAE #1 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4 |  |  | Each 60 Dense DAE included 8TB-60 drives
ECS |  | DAE #2 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #3 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #4 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #5 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #6 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #7 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
ECS |  | DAE #8 | 4 | - | 17.78 | 45 | 87.63 | 102 | 1146.6 | 1170 | 11.466 | 5.733 | 4000 | 200-240 | 5-35 | 8-90 | 4
PowerFlex | PowerFlex
PowerFlex | PowerFlex R640 | PowerFlex R640 1100W #1 | 1 | - | 4.28 | 48.2 | 80.9 | 21.9 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4100 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | *Dimensions include bezel. If a system with 1100 W AC or HVDC PSU operates from 100 to 120V, the power rating per PSU is derated
PowerFlex |  | PowerFlex R640 1600W #1 | 1 | - | 4.28 | 48.2 | 80.9 | 21.9 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 6000 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | *Dimensions include bezel. PSUs rated for 1600 W and higher require high-line voltage (200-240 V) to supply their rated capacity. If a system with 1600 W PSUs operates from 100 to 120 V, then the power rating per PSU is derated to 800
PowerFlex | PowerFlex R650 | PowerFlex R650 800W #1 | 1 | - | 4.28 | 48.2 | 82.284 | 21.2 | 800 | 842.1053 | 8.4211 | 4.2105 | 3140 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R650 1100W #1 | 1 | - | 4.28 | 48.2 | 82.284 | 21.2 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4300 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R650 1400W #1 | 1 | - | 4.28 | 48.2 | 82.284 | 21.2 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5460 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel. If a system with AC 1400 W PSUs operates at low line 100-120 Vac, then the power rating per PSU is degraded to 1050W.
PowerFlex | PowerFlex R740xd | PowerFlex R740xd 1100W #1 | 2 | - | 8.68 | 48.2 | 75.2 | 28.1 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4100 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R740xd 1600W #1 | 2 | - | 8.68 | 48.2 | 75.2 | 28.1 | 1600 | 1684.2105 | 16.8421 | 8.4211 | 6000 | 100-240 | 10-35 | 10-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R740xd 2000W #1 | 2 | - | 8.68 | 48.2 | 75.2 | 28.1 | 2000 | 2105.2632 | 21.0526 | 10.5263 | 7500 | 100-240 | 10-35 | 10-80 | 2 | C19 | C19/C20 | *Dimensions include bezel.
PowerFlex |  | PowerFlex R740xd 2400W #1 | 2 | - | 8.68 | 48.2 | 75.2 | 28.1 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 9000 | 100-240 | 10-35 | 10-80 | 2 | C19 | C19/C20 | *Dimensions include bezel.
PowerFlex | PowerFlex R750 | PowerFlex R750 800W #1 | 2 | - | 8.68 | 48.2 | 77.204 | 35.3 | 800 | 842.1053 | 8.4211 | 4.2105 | 3140 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R750 1100W #1 | 2 | - | 8.68 | 48.2 | 77.204 | 35.3 | 1100 | 1157.8947 | 11.5789 | 5.7895 | 4300 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel.
PowerFlex |  | PowerFlex R750 1400W #1 | 2 | - | 8.68 | 48.2 | 77.204 | 35.3 | 1400 | 1473.6842 | 14.7368 | 7.3684 | 5460 | 100-240 | 10-30 | 8-80 | 2 | C14 |  | *Dimensions include bezel. If a system with AC 1400 W PSUs operates at low line 100-120 Vac, then the power rating per PSU is degraded to 1050W.
PowerFlex |  | PowerFlex R750 2400W #1 | 2 | - | 8.68 | 48.2 | 77.204 | 35.3 | 2400 | 2526.3158 | 25.2632 | 12.6316 | 9210 | 100-240 | 10-30 | 8-80 | 2 | C19 | C19/C20 | *Dimensions include bezel.
RecoverPoint | RecoverPoint Gen6
RecoverPoint | RecoverPoint Gen6 | RPA Gen6 #1 | 1 | - | 4.47 | 44.45 | 79.33 | 27.21 | 677 | 720 | 7.7 | 3.6 | 2310 | 100-240 | 10-40 | 20-80 | 2 | C14
VPLEX | VPLEX VS6
VPLEX | Single-engine VS6 | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Base Engine | 4 | - | 17.7 | 47.9298 | 77.77 | 54.5 | 1114 | 1131 | N/A | 5.66 | 3800 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1430VA、1410W、4800Btu MMCSを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX | Dual-engine VS6 | UPS B | 1 | - | 4.37 | 48.01 | 38.1 | 12 | 6 | 6 | N/A | 0.03 | 0 | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14 | ※recahrge時 70VA、70W、200Btu
VPLEX |  | UPS A | 1 | - | 4.37 | 48.01 | 38.1 | 12 | 6 | 6 | N/A | 0.03 | 0 | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14 | ※recahrge時 70VA、70W、200Btu
VPLEX |  | IB-SW (2台) | 1 | - | 4.37 | 48.01 | 50.8 | 10 | 250 | 262 | N/A | 1.31 | 800 | 200-240 | 10-32 | 20-80 | - |  | -
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Engine #2 | 4 | - | 17.7 | 47.93 | 77.77 | 56 | 1096 | 1113 | N/A | 5.57 | 3700 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1410VA、1400W、4800Btu Akula Mangement Modulesを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Base Engine | 4 | - | 17.7 | 47.9298 | 77.77 | 56 | 1114 | 1131 | N/A | 5.66 | 3800 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1430VA、1410W、4800Btu MMCSを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | - |  | IEC320-C14
VPLEX | Quad-engine VS6 | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Engine #4 | 4 | - | 17.7 | 47.93 | 77.77 | 56 | 1096 | 1113 | N/A | 5.57 | 3700 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1410VA、1400W、4800Btu Akula Mangement Modulesを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Engine #3 | 4 | - | 17.7 | 47.93 | 77.77 | 56 | 1096 | 1113 | N/A | 5.57 | 3700 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1410VA、1400W、4800Btu Akula Mangement Modulesを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | UPS B | 1 | - | 4.37 | 48.01 | 38.1 | 12 | 6 | 6 | N/A | 0.03 | 0 | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14 | ※recahrge時 70VA、70W、200Btu
VPLEX |  | UPS A | 1 | - | 4.37 | 48.01 | 38.1 | 12 | 6 | 6 | N/A | 0.03 | 0 | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14 | ※recahrge時 70VA、70W、200Btu
VPLEX |  | IB-SW (2台) | 1 | - | 4.37 | 48.01 | 50.8 | 10 | 250 | 262 | N/A | 1.31 | 800 | 200-240 | 10-32 | 20-80 | - |  | -
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Engine #2 | 4 | - | 17.7 | 47.93 | 77.77 | 56 | 1096 | 1113 | N/A | 5.57 | 3700 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1410VA、1400W、4800Btu Akula Mangement Modulesを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | - | - | - | - |  | -
VPLEX |  | Base Engine | 4 | - | 17.7 | 47.9298 | 77.77 | 56 | 1114 | 1131 | N/A | 5.66 | 3800 | 200-240 | 10-32 | 20-80 | 4 |  | IEC320-C14 | ※recharge時 1430VA、1410W、4800Btu MMCSを含む
VPLEX |  | cable management assembly | 1 | - | 4.4 | - | 86.5 | - | - | - | - | - | - | 200-240 | 10-32 | 20-80 | - |  | IEC320-C14
VPLEX | VPLEX VS2
VPLEX | Single-engine VS2 | Management Server | 8 | - | 4.45 | 44.45 | 50.8 | 8.2 | 588 | 600 | N/A | 2.9 | 1900 | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14 | Engineの電源はSPSに2本接続を実施。 Unit数は予約スペース(ノード数x1U)を加味した値です。
VPLEX |  | Engin #1 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX | Dual-engine VS2 | Management Server | 22 | - | 4.45 | 44.45 | 50.8 | 8.2 | 1264.2 | 1290 | N/A | 6.2 | 4000 | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14 | Engineの電源はSPS に2本接続を実施。 Unit数は予約スペース(ノード数x1U)を加味した値です。
VPLEX |  | Engin #1 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | Engin #2 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | FC-SW #1 |  | - | 4.29 | 42.88 | 30.66 | 4.2 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14
VPLEX |  | FC-SW #2 |  | - | 4.29 | 42.88 | 30.66 | 4.2 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14
VPLEX |  | UPS A |  | - | 4.37 | 43.18 | 38.1 | 10 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | UPS B |  | - | 4.37 | 43.18 | 38.1 | 10 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX | Quad-engine VS2 | Management Server | 34 | - | 4.45 | 44.45 | 50.8 | 8.2 | 2273.6 | 2320 | N/A | 11.2 | 7200 | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14 | Engineの電源はSPSに2本接続を実施。 Unit数は予約スペース(ノード数x1U)を加味した値です。
VPLEX |  | Engin #1 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | Engin #2 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | Engin #3 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | Engin #4 |  | - | 8.89 | 44.45 | 61 | 23.4 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | N / A |  | N / A
VPLEX |  | SPS (2個分) |  | - | 8.56 | 41.9 | 43.18 | 28.8 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | FC-SW #1 |  | - | 4.29 | 42.88 | 30.66 | 4.2 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14
VPLEX |  | FC-SW #2 |  | - | 4.29 | 42.88 | 30.66 | 4.2 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 1 |  | IEC320-C14
VPLEX |  | UPS A |  | - | 4.37 | 43.18 | 38.1 | 10 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
VPLEX |  | UPS B |  | - | 4.37 | 43.18 | 38.1 | 10 |  |  | N/A |  |  | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14
Azure stack | AZURE STACK Hybrid
Azure stack | VxRack AZ-L | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. Hardware Lifecycle Host
Azure stack |  | R740xd HCI Node #1 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 665 | 669 | 6.69 | 3.35 | 2300 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #2 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 665 | 669 | 6.69 | 3.35 | 2300 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #3 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 665 | 669 | 6.69 | 3.35 | 2300 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #4 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 665 | 669 | 6.69 | 3.35 | 2300 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack | VxRack AZ-M | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. Hardware Lifecycle Host
Azure stack |  | R740xd HCI Node #1 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #2 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #3 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #4 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #5 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #6 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #7 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #8 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 739 | 743 | 7.43 | 3.72 | 2500 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack | VxRack AZ-H | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. ベゼルなし43.4cm Hardware Lifecycle Host
Azure stack |  | R740xd HCI Node #1 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #2 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #3 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #4 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #5 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #6 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #7 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #8 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #9 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #10 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #11 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack |  | R740xd HCI Node #12 | 2 | - | 8.68 | 48.2 | 71.55 | 33 | 798 | 802 | 8.02 | 4.01 | 2700 | 100-240 | 0-30 | 10-80 | 2 |  |  | 幅:ベゼルあり。ベゼルなし43.4cm 奥行:ベゼルなし、背面のパーツ含む
Azure stack | AZURE STACK All Flash
Azure stack | VxRack AZ-L | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm Hardware Lifecycle Host
Azure stack |  | R640 AFL Node #1 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 436 | 446 | 4.46 | 2.23 | 1500 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFL=All Flash Low Capacity
Azure stack |  | R640 AFL Node #2 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 436 | 446 | 4.46 | 2.23 | 1500 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFL=All Flash Low Capacity
Azure stack |  | R640 AFL Node #3 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 436 | 446 | 4.46 | 2.23 | 1500 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFL=All Flash Low Capacity
Azure stack |  | R640 AFL Node #4 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 436 | 446 | 4.46 | 2.23 | 1500 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFL=All Flash Low Capacity
Azure stack | VxRack AZ-H | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5248F-ON #1 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | S5248F-ON #2 | 1 | - | 4.4 | 43.4 | 46 | 9.7 | 602 | 633.6842 | 6.02 | 3.01 | 2054.11 | 100-240 | 5-45 | 5-90 | 2 |  | NEMA5-15 IEC320-C14
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm Hardware Lifecycle Host
Azure stack |  | R640 AFH Node #1 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #2 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #3 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #4 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #5 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #6 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #7 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #8 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #9 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #10 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #11 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack |  | R640 AFH Node #12 | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 576 | 583 | 5.83 | 2.92 | 2000 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm AFH=All Flash Hgih Capacity
Azure stack | AZURE STACK R840 | S3048-ON | 1 | - | 4.4 | 43.4 | 32 | 6,74 | 200 | 210.5263 | 2 | 1 | 682.43 | 90-264 | 0-45 | 5-85 | 2 |  |  | with 2PS 定格消費電力
Azure stack |  | S5048F-ON #1 | 1 | - | 4.35 | 43.4 | 45.7 | 9.98 | 750 | 789.4737 | 7.5 | 3.75 | 2559.11 | 100-240 | 0-45 | 10-85 | 2 |  |  | 定格消費電力
Azure stack |  | S5048F-ON #2 | 1 | - | 4.35 | 43.4 | 45.7 | 9.98 | 750 | 789.4737 | 7.5 | 3.75 | 2559.11 | 100-240 | 0-45 | 10-85 | 2 |  |  | 定格消費電力
Azure stack |  | R640 Management Node | 1 | - | 4.28 | 48.2 | 80.85 | 21.9 | 236 | 244 | 2.44 | 1.22 | 800 | 100-240 | 0-30 | 10-80 | 2 |  |  | ※Dimensions include bezel. 幅:ベゼルなし43.4cm Hardware Lifecycle Host
Azure stack |  | R840 AFH Node #1 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #2 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #3 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #4 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #5 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #6 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #7 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #8 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #9 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #10 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #11 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
Azure stack |  | R840 AFH Node #12 | 2 | - | 8.68 | 48.2 | 94 | 36.6 | 1190 | 1200 | 12 | 6 | 4100 | 100-240 | 10-35 | 5-85 | 2
DLm | Disk Library for Mainframe (DLm) Gen5
DLm | DLm2500 | VTE#1 | 2 | - | 8.68 | 43.38 | 70.1 | 33 | 384.9 | 386.7 | 3.87 | 1.93 | 1313 | 90-264 | 10-30 | 20-80 | 2 | C14 | C13/C14 & NEMAL6-30P | 210-AZIVに200Vバンドル。Each power supply provides 750 Watts of power and is self-selecting, operating at 100-120V or 200-240V.
DLm | DLm8500 Single Rack Solution for DataDomain/PowerScale | 10GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #2 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | N3248TE-ON #2 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | 1GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#2 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm | DLm8500 Single Rack with DD6300/DD6800/DD9300 and ES30 DAEs (Minimum) | Air buffer | 15 | - | 66 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | DD6300 (12HDD) | 2 | - | 8.7 | 48.26 | 77.47 | 37.2 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | Air buffer | 3 | - | 13.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Sliding tray ※EMC rack | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
DLm |  | Air buffer | 3 | - | 13.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | ES30 #2 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | up to 8*ES30 drive drawers
DLm |  | ES30 #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | up to 8*ES30 drive drawers
DLm |  | 10GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | 1GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Air buffer | 2 | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm | DLm8500 Single Rack with DD6300/DD6800/DD9300 and ES30 DAEs (Maximum) | ES30 #8 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
DLm |  | ES30 #7 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2
DLm |  | ES30 #6 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | ES30 #5 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | DD6300 (12HDD) #2 | 2 | - | 8.7 | 48.26 | 77.47 | 37.2 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | DD6300 (12HDD) #1 | 2 | - | 8.7 | 48.26 | 77.47 | 37.2 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | ES30 #4 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | Sliding tray ※EMC rack | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
DLm |  | ES30 #3 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | ES30 #2 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | ES30 #1 | 3 | - | 13.34 | 45 | 35.56 | 30.8 | 235 | 280 | 2.8 | 1.4 | 800 | 100-240 | 10-35 | 20-80 | 2 | C14
DLm |  | 10GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #2 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | N3248TE-ON #2 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | 1GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#2 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm | DLm8500 Single Rack with DD6800/DD9300 and DS60 DAEs (Minimum) | Air buffer | 15 | - | 66 | - |  | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | DD6300 (12HDD) | 2 | - | 8.7 | 48.26 | 77.47 | 37.2 | 530 | 773 | 5.3 | 2.65 | 1808 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | Air buffer | 2 | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Sliding tray ※EMC rack | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
DLm |  | Air buffer | 5 | - | 22 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 90.7 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DLm |  | 10GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | 1GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Air buffer | 2 | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm | DLm8500 Single Rack with DD6800/DD9300 and DS60 DAEs (Maximum) | Air buffer | 12 | - | 52.8 | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | DD6800 (4HDD+2SSD) #1 | 2 | - | 8.7 | 48.26 | 77.47 | 31 | 560 | 794 | 5.6 | 2.8 | 1910 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | DD6800 (4HDD+2SSD) #1 | 2 | - | 8.7 | 48.26 | 77.47 | 31 | 560 | 794 | 5.6 | 2.8 | 1910 | 100-240 | 10-35 | 20-80 | 2 | C14 |  | DDは構成されるモデルによって変更してください。
DLm |  | Air buffer | 2 | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Sliding tray ※EMC rack | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
DLm |  | DS60 #2 | 5 | - | 22.23 | 44.45 | 92.46 | 90.7 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DLm |  | DS60 #1 | 5 | - | 22.23 | 44.45 | 92.46 | 90.7 | 931 | 980 | - | 4.9 | 3177 | 200-240 | 5-40 | 20-80 | 4 | C14 | C13/C14 | Weight:With FRUs installed Unit: including a 1U Cable Managements Tray.
DLm |  | 10GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #2 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | N3248TE-ON #2 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | 1GbE cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#2 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm | DLm8500 VTEC Components in a Multiple Rack | Air buffer | 8 | - | 35.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#8 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0 7th and 8th VTE are available by RPQ
DLm |  | VTE#7 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0 7th and 8th VTE are available by RPQ
DLm |  | VTE#6 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#5 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | Air buffer | 4 | - | 17.6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | Sliding tray ※EMC rack | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | 1 | C14 | C13/C14
DLm |  | Air buffer | 1 | - | 4.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #2 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | open for switch power cords | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | S4148F-ON #1 | 1 | - | 4.4 | 43.1 | 45.7 | 9.6 | 370 | 389.4737 | 3.8947 | 1.9474 | 1262 | 100-240 | 5-40 | 5-85 | 2 | C14
DLm |  | cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | N3248TE-ON #2 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | open for switch power cords | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | N3248TE-ON #1 | 1 | - | 4.34 | 43.4 | 42.3 | 6.99 | 212 | 223.1579 | 2.12 | 1.06 | 723.38 | 100-240 | 5-95 | 2 | 2 | C14 |  | ※MAX消費電力、定格消費電力:550W
DLm |  | cable management | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm |  | VTE#4 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#3 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#2 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | VTE#1 | 2 | - | 8.68 | 43.4 | 71.55 | 33 | 382.2 | 390 | 3.822 | 1.911 | 1300 | 100-240 | 0-45 | 5-85 | 2 | C14 |  | based on Dell 14G R740xl server 消費電力、発熱量はPC3.0
DLm |  | Air buffer | 2 | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
DLm | Disk Library for Mainframe (DLm) Gen4
DLm | DLm2100 with Data Domain | DLm2100 | 2 | - | 8.75 | 43 | 67.2 | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | 90-264 | 10-30 | 20-80 | 2 |  |  | ラックは40U-C ラック無しの諸元値
DLm |  | Data Domain | DDの諸元に準ずる
DLm | DLm2100 with VNX | DLm2100 for VNX | 40 | - | 194.7 | 61 | 106.4 | 603 | 5448.8 | 5560 | 54.488 | 27.244 | 17700 | 200-240 | 10-32 | 20-80 | 2 |  | IEC320-C14 | ラックは40U-C ラック込みの諸元値
DLm | DLm8100 with VMAX | VTEC Bay | 40 | - | 194.7 | 61 | 106.4 | 487.7 | 3332 | 3400 | 33.32 | 16.66 | 11400 | 200-240 | 10-32 | 20-80 | 2 |  | NEMA L6-30 | ラックは40U-C
DLm |  | Storage controller Bay(VG8) | VG8＆DS6510の諸元に準ずる | [16 empty] | ラックは40U-C
DLm |  | VMAX system Bay | VMAXの諸元に準ずる | [15 empty] | NEMA L6-30 | 重量：8DMの場合
DLm |  | VMAX storage Bay | VMAXの諸元に準ずる | [15 empty] | NEMA L6-30
DLm | DLm8100 with VNX or Data Domain | VTEC Bay | 40 | - | 194.7 | 61 | 106.4 | 480.81 | 3626 | 3700 | 36.26 | 18.13 | 12300 | 200-240 | 10-32 | 20-80 | 2 |  | NEMA L6-30 | ラックは40U-C
DLm |  | VNX Bay | VNXの諸元に準ずる
DLm |  | Storage Bay | VNXの諸元に準ずる | [16 empty] | VNXで2ラック以上の構成がある場合に限る
DLm |  | Data Domain Bay | DDの諸元に準ずる
DLm | DLm8100 VTEC-Bay | Air buffer | 10 | - | - | - |  | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | AT-9924TL 1GbE Management Switch#1 | 1 | - | 4.45 | 44 | 44 | 7.7 | 60 | 63.1579 | 0.6 | 0.3 | 204.7285 | 100-240 | 0-50 | 5-80
DLm |  | empty space | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | AT-9924TL 1GbE Management Switch#2 | 1 | - | 4.45 | 44 | 44 | 7.7 | 60 | 63.1579 | 0.6 | 0.3 | 204.7285 | 100-240 | 0-50 | 5-80
DLm |  | cable management tray | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | VDX6740 10GbE Switch#1 | 1 | - | 4.318 | 43.99 | 40.99 | 8.66 | 110 | 115.7895 | 1.1 | 0.55 | 1672.41 | 85-264 | 0-40 | 10-85 | 2
DLm |  | empty space | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | VDX6740 10GbE Switch#2 | 1 | - | 4.318 | 43.99 | 40.99 | 8.66 | 110 | 115.7895 | 1.1 | 0.55 | 1672.41 | 85-264 | 0-40 | 10-85 | 2
DLm |  | cable management tray | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | Sliding Tray | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | empty space | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | cable management tray | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
DLm |  | Virtual Tape Emulation#1 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#2 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#3 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#4 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#5 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#6 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#7 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | Virtual Tape Emulation#8 | 2 | - | - | - | - | 27 | 352.8 | 360 | 3.528 | 1.764 | 1200 | - | - | -
DLm |  | empty space | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -